## Sheet1
Analysis of rate
1.1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.1.1 | Group A |  | DSR | Rate Rs. | 659
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 7.88 | 11.1 | 87.47
= 2x3+1x1.5= 7.5 + 0.38 (wastage @ 5%) = 7.88 m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 2.63 | 60.01 | 157.83
= 2.5 + 0.13 (wastage @ 5%) = 2.63 m
1206 | 20 mm inspection/ solid bends | each | 1 | 7.61 | 7.61
1211 | 20 mm sockets | each | 0 | 6.93 | 0
1218 | 20 mm iron staples/ saddles/ screws | each | 4 | 1.6 | 6.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 8 | 0.4 | 3.2
2920 | Washers | each | 4 | 0.17 | 0.68
1306 | 75 mm X 75 mm X 60 mm deep metal box | each | 1 | 20 | 20
1322 | 3 mm thick phenolic laminated sheet | sqcm | 72 | 0.1 | 7.2
1216 | 20 mm junction box, one way | each | 1 | 17.86 | 17.86
1431 | S.P. 5/6 amps, one way switch, piano type ISI marked | each | 1 | 13.3 | 13.3
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 327.17
| Cartage @ 1 % of A1 |  |  |  | 3.2717
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 572.9817
| OVERHEADS & PROFIT @ 15 % |  |  |  | 85.95
| TOTAL |  |  |  | 658.9317
| Rate per point |  |  |  | 658.9317
| Say |  |  |  | 659
659
Analysis of rate
1.1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.1.2 | Group B |  | DSR | Rate Rs. | 793
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 10.5 | 11.1 | 116.55
= 2x4+1x2 = 10 + 0.50 (wastage @ 5%) = 10.5m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 3.68 | 60.01 | 220.84
= 3.5 + 0.18 (wastage @ 5%) = 3.68m
1206 | 20 mm inspection/ solid bends | each | 1 | 7.61 | 7.61
1211 | 20 mm sockets | each | 2 | 6.93 | 13.86
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 8 | 0.4 | 3.2
2920 | Washers | each | 4 | 0.17 | 0.68
1306 | 75 mm X 75 mm X 60 mm deep metal box | each | 1 | 20 | 20
1322 | 3 mm thick phenolic laminated sheet | sqcm | 72 | 0.1 | 7.2
1216 | 20 mm junction box, one way | each | 1 | 17.86 | 17.86
1431 | S.P. 5/6 amps, one way switch, piano type ISI marked | each | 1 | 13.3 | 13.3
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 442.52
| Cartage @ 1 % of A1 |  |  |  | 4.4252
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 689.4852
| OVERHEADS & PROFIT @ 15 % |  |  |  | 103.42
| TOTAL |  |  |  | 792.9052
| Rate per point |  |  |  | 792.9052
| Say |  |  |  | 793
793
Analysis of rate
1.1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.1.3 | Group C |  | DSR | Rate Rs. | 994
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 13.15 | 11.1 | 145.97
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%) = 13.15m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 4.73 | 60.01 | 283.85
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
1206 | 20 mm inspection/ solid bends | each | 1 | 7.61 | 7.61
1211 | 20 mm sockets | each | 2 | 6.93 | 13.86
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 8 | 0.4 | 3.2
2920 | Washers | each | 4 | 0.17 | 0.68
1306 | 75 mm X 75 mm X 60 mm deep metal box | each | 1 | 20 | 20
1322 | 3 mm thick phenolic laminated sheet | sqcm | 72 | 0.1 | 7.2
1216 | 20 mm junction box, one way | each | 1 | 17.86 | 17.86
1431 | S.P. 5/6 amps, one way switch, piano type ISI marked | each | 1 | 13.3 | 13.3
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 534.95
| Cartage @ 1 % of A1 |  |  |  | 5.3495
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 864.3395
| OVERHEADS & PROFIT @ 15 % |  |  |  | 129.65
| TOTAL |  |  |  | 993.9895
| Rate per point |  |  |  | 993.9895
| Say |  |  |  | 994
994
Analysis of rate
1.2 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, 2 way piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
|  |  | DSR | Rate Rs. | 999
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 13.15 | 11.1 | 145.97
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%) = 13.15m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 4.73 | 60.01 | 283.85
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
1206 | 20 mm inspection/ solid bends | each | 1 | 7.61 | 7.61
1211 | 20 mm sockets | each | 2 | 6.93 | 13.86
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 8 | 0.4 | 3.2
2920 | Washers | each | 4 | 0.17 | 0.68
1306 | 75 mm X 75 mm X 60 mm deep metal box | each | 1 | 20 | 20
1322 | 3 mm thick phenolic laminated sheet | sqcm | 72 | 0.1 | 7.2
1216 | 20 mm junction box, one way | each | 1 | 17.86 | 17.86
1432 | S.P. 5/6 amps, two way switch, piano type ISI marked | each | 1 | 17.37 | 17.37
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 539.02
| Cartage @ 1 % of A1 |  |  |  | 5.3902
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 868.4502
| OVERHEADS & PROFIT @ 15 % |  |  |  | 130.27
| TOTAL |  |  |  | 998.73
| Rate per point |  |  |  | 998.73
| Say |  |  |  | 999
999
Analysis of rate
1.3 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.3.1 | Group A |  | DSR | Rate Rs. | 702
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 7.88 | 11.1 | 87.47
= 2x3+1x1.5= 7.5 + 0.38 (wastage @ 5%) = 7.88 m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 2.63 | 60.01 | 157.83
= 2.5 + 0.13 (wastage @ 5%) = 2.63 m
1206 | 20 mm inspection/ solid bends | each | 1 | 7.61 | 7.61
1211 | 20 mm sockets | each | 0 | 6.93 | 0
1218 | 20 mm iron staples/ saddles/ screws | each | 4 | 1.6 | 6.4
1216 | 20 mm junction box, one way | each | 1 | 17.86 | 17.86
1300 | Modular GI box for 2 module | each | 0.5 | 28 | 14
1421 | Modular base & cover plate for 2 module | each | 0.5 | 39.6 | 19.8
1402 | S.P. 5/6 amps, one way modular switch, ISI marked | each | 1 | 48 | 48
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 364.59
| Cartage @ 1 % of A1 |  |  |  | 3.6459
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 610.7759
| OVERHEADS & PROFIT @ 15 % |  |  |  | 91.62
| TOTAL |  |  |  | 702.3959
| Rate per point |  |  |  | 702.3959
| Say |  |  |  | 702
702
Analysis of rate
1.3 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.3.2 | Group B |  | DSR | Rate Rs. | 836
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 10.5 | 11.1 | 116.55
= 2x4+1x2 = 10 + 0.50 (wastage @ 5%) = 10.5m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 3.68 | 60.01 | 220.84
= 3.5 + 0.18 (wastage @ 5%) = 3.68m
1206 | 20 mm inspection/ solid bends | each | 1 | 7.61 | 7.61
1211 | 20 mm sockets | each | 2 | 6.93 | 13.86
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
1216 | 20 mm junction box, one way | each | 1 | 17.86 | 17.86
1300 | Modular GI box for 2 module | each | 0.5 | 28 | 14
1421 | Modular base & cover plate for 2 module | each | 0.5 | 39.6 | 19.8
1402 | S.P. 5/6 amps, one way modular switch, ISI marked | each | 1 | 48 | 48
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 479.94
| Cartage @ 1 % of A1 |  |  |  | 4.7994
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 727.2794
| OVERHEADS & PROFIT @ 15 % |  |  |  | 109.09
| TOTAL |  |  |  | 836.3694
| Rate per point |  |  |  | 836.3694
| Say |  |  |  | 836
836
Analysis of rate
1.3 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.3.3 | Group C |  | DSR | Rate Rs. | 1037
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 13.15 | 11.1 | 145.97
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%) = 13.15m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 4.73 | 60.01 | 283.85
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
1206 | 20 mm inspection/ solid bends | each | 1 | 7.61 | 7.61
1211 | 20 mm sockets | each | 2 | 6.93 | 13.86
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
1216 | 20 mm junction box, one way | each | 1 | 17.86 | 17.86
1300 | Modular GI box for 2 module | each | 0.5 | 28 | 14
1421 | Modular base & cover plate for 2 module | each | 0.5 | 39.6 | 19.8
1402 | S.P. 5/6 amps, one way modular switch, ISI marked | each | 1 | 48 | 48
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 572.37
| Cartage @ 1 % of A1 |  |  |  | 5.7237
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 902.1337
| OVERHEADS & PROFIT @ 15 % |  |  |  | 135.32
| TOTAL |  |  |  | 1037.4537
| Rate per point |  |  |  | 1037.4537
| Say |  |  |  | 1037
1037
Analysis of rate
1.4 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
|  |  | DSR | Rate Rs. | 1094
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 13.15 | 11.1 | 145.97
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%) = 13.15m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 4.73 | 60.01 | 283.85
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
1206 | 20 mm inspection/ solid bends | each | 1 | 7.61 | 7.61
1211 | 20 mm sockets | each | 2 | 6.93 | 13.86
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
1216 | 20 mm junction box, one way | each | 1 | 17.86 | 17.86
1217 | 20 mm junction box, two way | each | 2 | 17.86 | 35.72
1300 | Modular GI box for 2 module | each | 0.5 | 28 | 14
1421 | Modular base & cover plate for 2 module | each | 0.5 | 39.6 | 19.8
1403 | S.P. 5/6 amps, two way modular switch, ISI marked | each | 1 | 60.8 | 60.8
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 620.89
| Cartage @ 1 % of A1 |  |  |  | 6.2089
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 951.1389
| OVERHEADS & PROFIT @ 15 % |  |  |  | 142.67
| TOTAL |  |  |  | 1093.8089
| Rate per point |  |  |  | 1093.8089
| Say |  |  |  | 1094
1094
Analysis of rate
1.5 | Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required.
|  |  | DSR | Rate Rs. | 239
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 26.18 | 4164.71
= 50.5x3=151.5+7.58(Wastage @ 5%)=159.08m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 52.5 | 60.01 | 3150.53
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1206 | 20 mm inspection/ solid bends | each | 4 | 7.61 | 30.44
1211 | 20 mm sockets | each | 10 | 6.93 | 69.3
1217 | 20 mm junction box, two way | each | 6 | 17.86 | 107.16
1218 | 20 mm iron staples/ saddles/ screws | each | 85 | 1.6 | 136
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 7686.44
| Cartage @ 1 % of A1 |  |  |  | 76.8644
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 10384.0944
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1557.61
| TOTAL |  |  |  | 11941.7044
| Rate per meter |  |  |  | 238.8341
| Say |  |  |  | 239
239
Analysis of rate
1.6 | Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit alongwith 2 Nos 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required.
|  |  | DSR | Rate Rs. | 366
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 26.18 | 8329.17
=50.5x6=303.0+15.15(Wastage @ 5%)=318.15m
1202 | 25 mm dia. ISI marked, steel conduit | metre | 52.5 | 75.6 | 3969
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1207 | 25 mm inspection/ solid bends | each | 4 | 13.39 | 53.56
1212 | 25 mm sockets | each | 10 | 7.56 | 75.6
1217 | 20 mm junction box, two way | each | 6 | 17.86 | 107.16
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 12748.94
| Cartage @ 1 % of A1 |  |  |  | 127.4894
LABOUR
1001 | Wireman | day | 3 | 447 | 1341
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 3.75 | 368 | 1380
| TOTAL |  |  |  | 15904.7194
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2385.71
| TOTAL |  |  |  | 18290.4294
| Rate per meter |  |  |  | 365.8086
| Say |  |  |  | 366
366
Analysis of rate
1.7 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.1 | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire |  | DSR | Rate Rs. | 181
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 11.1 | 1765.79
= 50.5x3=151.5+7.58(Wastage @ 5%)=159.08m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 52.5 | 60.01 | 3150.53
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1206 | 20 mm inspection/ solid bends | each | 4 | 7.61 | 30.44
1211 | 20 mm sockets | each | 15 | 6.93 | 103.95
1218 | 20 mm iron staples/ saddles/ screws | each | 85 | 1.6 | 136
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 5215.01
| Cartage @ 1 % of A1 |  |  |  | 52.1501
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 7887.9501
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1183.19
| TOTAL |  |  |  | 9071.1401
| Rate per meter |  |  |  | 181.4228
| Say |  |  |  | 181
181
Analysis of rate
1.7 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.2 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire |  | DSR | Rate Rs. | 206
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 17.84 | 2837.99
= 50.5x3=151.5+7.58(Wastage @ 5%)=159.08m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 52.5 | 60.01 | 3150.53
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1206 | 20 mm inspection/ solid bends | each | 4 | 7.61 | 30.44
1211 | 20 mm sockets | each | 15 | 6.93 | 103.95
1218 | 20 mm iron staples/ saddles/ screws | each | 85 | 1.6 | 136
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 6287.21
| Cartage @ 1 % of A1 |  |  |  | 62.8721
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 8970.8721
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1345.63
| TOTAL |  |  |  | 10316.5021
| Rate per meter |  |  |  | 206.33
| Say |  |  |  | 206
206
Analysis of rate
1.7 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.3 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire |  | DSR | Rate Rs. | 237
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 26.18 | 4164.71
= 50.5x3=151.5+7.58(Wastage @ 5%)=159.08m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 52.5 | 60.01 | 3150.53
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1206 | 20 mm inspection/ solid bends | each | 4 | 7.61 | 30.44
1211 | 20 mm sockets | each | 15 | 6.93 | 103.95
1218 | 20 mm iron staples/ saddles/ screws | each | 85 | 1.6 | 136
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 7613.93
| Cartage @ 1 % of A1 |  |  |  | 76.1393
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 10310.8593
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1546.63
| TOTAL |  |  |  | 11857.4893
| Rate per meter |  |  |  | 237.1498
| Say |  |  |  | 237
237
Analysis of rate
1.7 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.4 | 2 X 6 sq. mm + 1 X 6 sq. mm earth wire |  | DSR | Rate Rs. | 324
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 38.87 | 6183.44
= 50.5x3=151.5+7.58(Wastage @ 5%)=159.08m
1202 | 25 mm dia. ISI marked, steel conduit | metre | 52.5 | 75.6 | 3969
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1207 | 25 mm inspection/ solid bends | each | 4 | 13.39 | 53.56
1212 | 25 mm sockets | each | 15 | 7.56 | 113.4
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 10533.85
| Cartage @ 1 % of A1 |  |  |  | 105.3385
LABOUR
1001 | Wireman | day | 3.5 | 447 | 1564.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 4.25 | 368 | 1564
| TOTAL |  |  |  | 14074.9785
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2111.25
| TOTAL |  |  |  | 16186.2285
| Rate per meter |  |  |  | 323.7246
| Say |  |  |  | 324
324
Analysis of rate
1.7 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.5 | 2 X 10 sq. mm + 1 X 10 sq. mm earth wire |  | DSR | Rate Rs. | 392
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1105 | 10 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5x2=101.0+5.05(Wastage @ 5%)=106.05m | metre | 106.05 | 66.43 | 7044.9
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5+2.53(Wastage @ 5%)=53.03m | metre | 53.03 | 38.87 | 2061.28
1202 | 25 mm dia. ISI marked, steel conduit | metre | 52.5 | 75.6 | 3969
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1207 | 25 mm inspection/ solid bends | each | 4 | 13.39 | 53.56
1212 | 25 mm sockets | each | 15 | 7.56 | 113.4
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 13456.59
| Cartage @ 1 % of A1 |  |  |  | 134.5659
LABOUR
1001 | Wireman | day | 3.5 | 447 | 1564.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 4.25 | 368 | 1564
| TOTAL |  |  |  | 17026.9459
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2554.04
| TOTAL |  |  |  | 19580.9859
| Rate per meter |  |  |  | 391.6197
| Say |  |  |  | 392
392
Analysis of rate
1.7 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.6 | 2 X 16 sq. mm + 1 X 16 sq. mm earth wire |  | DSR | Rate Rs. | 530
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1106 | 16 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5x2=101.0+5.05(Wastage @ 5%)=106.05m | metre | 106.05 | 102.36 | 10855.28
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5+2.53(Wastage @ 5%)=53.03m | metre | 53.03 | 38.87 | 2061.28
1203 | 32 mm dia. ISI marked, steel conduit | metre | 52.5 | 113.4 | 5953.5
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1208 | 32 mm inspection/ solid bends | each | 4 | 25.2 | 100.8
1213 | 32 mm sockets | each | 15 | 9.77 | 146.55
1220 | 32 mm iron staples/ saddles/ screws | each | 85 | 3.34 | 283.9
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 19429.61
| Cartage @ 1 % of A1 |  |  |  | 194.2961
LABOUR
1001 | Wireman | day | 3.5 | 447 | 1564.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 4.25 | 368 | 1564
| TOTAL |  |  |  | 23059.6961
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3458.95
| TOTAL |  |  |  | 26518.6461
| Rate per meter |  |  |  | 530.3729
| Say |  |  |  | 530
530
Analysis of rate
1.7 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.7 | 4 X 2.5 sq. mm + 2 X 2.5 sq. mm earth wire |  | DSR | Rate Rs. | 312
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 17.84 | 5675.8
=50.5x6=303.0+15.15(Wastage @ 5%)=318.15m
1202 | 25 mm dia. ISI marked, steel conduit | metre | 52.5 | 75.6 | 3969
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1207 | 25 mm inspection/ solid bends | each | 4 | 13.39 | 53.56
1212 | 25 mm sockets | each | 15 | 7.56 | 113.4
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 10026.21
| Cartage @ 1 % of A1 |  |  |  | 100.2621
LABOUR
1001 | Wireman | day | 3.5 | 447 | 1564.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 4.25 | 368 | 1564
| TOTAL |  |  |  | 13562.2621
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2034.34
| TOTAL |  |  |  | 15596.6021
| Rate per meter |  |  |  | 311.932
| Say |  |  |  | 312
312
Analysis of rate
1.7 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.8 | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire |  | DSR | Rate Rs. | 374
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 26.18 | 8329.17
=50.5x6=303.0+15.15(Wastage @ 5%)=318.15m
1202 | 25 mm dia. ISI marked, steel conduit | metre | 52.5 | 75.6 | 3969
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1207 | 25 mm inspection/ solid bends | each | 4 | 13.39 | 53.56
1212 | 25 mm sockets | each | 15 | 7.56 | 113.4
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 12679.58
| Cartage @ 1 % of A1 |  |  |  | 126.7958
LABOUR
1001 | Wireman | day | 3.5 | 447 | 1564.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 4.25 | 368 | 1564
| TOTAL |  |  |  | 16242.1658
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2436.32
| TOTAL |  |  |  | 18678.4858
| Rate per meter |  |  |  | 373.5697
| Say |  |  |  | 374
374
Analysis of rate
1.7 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.9 | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire |  | DSR | Rate Rs. | 518
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 38.87 | 12366.49
=50.5x6=303.0+15.15(Wastage @ 5%)=318.15m
1203 | 32 mm dia. ISI marked, steel conduit | metre | 52.5 | 113.4 | 5953.5
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1208 | 32 mm inspection/ solid bends | each | 4 | 25.2 | 100.8
1213 | 32 mm sockets | each | 15 | 9.77 | 146.55
1220 | 32 mm iron staples/ saddles/ screws | each | 85 | 3.34 | 283.9
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 18879.54
| Cartage @ 1 % of A1 |  |  |  | 188.7954
LABOUR
1001 | Wireman | day | 3.5 | 447 | 1564.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 4.25 | 368 | 1564
| TOTAL |  |  |  | 22504.1254
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3375.62
| TOTAL |  |  |  | 25879.7454
| Rate per meter |  |  |  | 517.5949
| Say |  |  |  | 518
518
Analysis of rate
1.7 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.10 | 4 X 10 sq. mm + 2 X 10 sq. mm earth wire |  | DSR | Rate Rs. | 653
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1105 | 10 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable=50.5x4=202.0+10.10(Wastage @ 5%)=212.10m | metre | 212.1 | 66.43 | 14089.8
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5x2=101.0+5.05(Wastage @ 5%)=106.05m | metre | 106.05 | 38.87 | 4122.16
1203 | 32 mm dia. ISI marked, steel conduit | metre | 52.5 | 113.4 | 5953.5
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1208 | 32 mm inspection/ solid bends | each | 4 | 25.2 | 100.8
1213 | 32 mm sockets | each | 15 | 9.77 | 146.55
1220 | 32 mm iron staples/ saddles/ screws | each | 85 | 3.34 | 283.9
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24725.01
| Cartage @ 1 % of A1 |  |  |  | 247.2501
LABOUR
1001 | Wireman | day | 3.5 | 447 | 1564.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 4.25 | 368 | 1564
| TOTAL |  |  |  | 28408.0501
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4261.21
| TOTAL |  |  |  | 32669.2601
| Rate per meter |  |  |  | 653.3852
| Say |  |  |  | 653
653
Analysis of rate
1.7 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
1.7.11 | 4 X 16 sq. mm + 2 X 16 sq. mm earth wire |  | DSR | Rate Rs. | 930
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1106 | 16 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable=50.5x4=202.0+10.10(Wastage @ 5%)=212.10m | metre | 212.1 | 102.36 | 21710.56
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5x2=101.0+5.05(Wastage @ 5%)=106.05m | metre | 106.05 | 38.87 | 4122.16
1204 | 40 mm dia. ISI marked, steel conduit | metre | 52.5 | 184.28 | 9674.7
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1209 | 40 mm inspection/ solid bends | each | 4 | 34.13 | 136.52
1214 | 40 mm sockets | each | 15 | 13.86 | 207.9
1221 | 40 mm iron staples/ saddles/ screws | each | 85 | 4.31 | 366.35
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 36246.49
| Cartage @ 1 % of A1 |  |  |  | 362.4649
LABOUR
1001 | Wireman | day | 4 | 447 | 1788
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.01 | 407 | 4.07
1007 | Khallasi | day | 4.75 | 368 | 1748
| TOTAL |  |  |  | 40454.2749
| OVERHEADS & PROFIT @ 15 % |  |  |  | 6068.14
| TOTAL |  |  |  | 46522.4149
| Rate per meter |  |  |  | 930.4483
| Say |  |  |  | 930
930
Analysis of rate
1.8 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size M.S. box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.8.1 | Group A |  | DSR | Rate Rs. | 504
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 7.88 | 11.1 | 87.47
= 2x3+1x1.5= 7.5 + 0.38 (wastage @ 5%) = 7.88 m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 2.63 | 11.81 | 31.06
= 2.5 + 0.13 (wastage @ 5%) = 2.63 m
1229 | 20 mm PVC bends | each | 1 | 5.65 | 5.65
1234 | 20 mm PVC couplers | each | 0 | 3.5 | 0
1218 | 20 mm iron staples/ saddles/ screws | each | 4 | 1.6 | 6.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 8 | 0.4 | 3.2
2920 | Washers | each | 4 | 0.17 | 0.68
1306 | 75 mm X 75 mm X 60 mm deep metal box | each | 1 | 20 | 20
1322 | 3 mm thick phenolic laminated sheet | sqcm | 72 | 0.1 | 7.2
1239 | 20 mm PVC junction box, one way | each | 1 | 15.45 | 15.45
1431 | S.P. 5/6 amps, one way switch, piano type ISI marked | each | 1 | 13.3 | 13.3
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 196.03
| Cartage @ 1 % of A1 |  |  |  | 1.9603
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 438.4903
| OVERHEADS & PROFIT @ 15 % |  |  |  | 65.77
| TOTAL |  |  |  | 504.2603
| Rate per point |  |  |  | 504.2603
| Say |  |  |  | 504
504
Analysis of rate
1.8 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size M.S. box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required
1.8.2 | Group B |  | DSR | Rate Rs. | 571
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 10.5 | 11.1 | 116.55
= 2x4+1x2 = 10 + 0.50 (wastage @ 5%) = 10.5m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 3.68 | 11.81 | 43.46
= 3.5 + 0.18 (wastage @ 5%) = 3.68m
1229 | 20 mm PVC bends | each | 1 | 5.65 | 5.65
1234 | 20 mm PVC couplers | each | 2 | 3.5 | 7
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 8 | 0.4 | 3.2
2920 | Washers | each | 4 | 0.17 | 0.68
1306 | 75 mm X 75 mm X 60 mm deep metal box | each | 1 | 20 | 20
1322 | 3 mm thick phenolic laminated sheet | sqcm | 72 | 0.1 | 7.2
1239 | 20 mm PVC junction box, one way | each | 1 | 15.45 | 15.45
1431 | S.P. 5/6 amps, one way switch, piano type ISI marked | each | 1 | 13.3 | 13.3
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 253.91
| Cartage @ 1 % of A1 |  |  |  | 2.5391
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 496.9491
| OVERHEADS & PROFIT @ 15 % |  |  |  | 74.54
| TOTAL |  |  |  | 571.4891
| Rate per point |  |  |  | 571.4891
| Say |  |  |  | 571
571
Analysis of rate
1.8 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size M.S. box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required
1.8.3 | Group C |  | DSR | Rate Rs. | 714
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 13.15 | 11.1 | 145.97
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%) = 13.15m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 4.73 | 11.81 | 55.86
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
1229 | 20 mm PVC bends | each | 1 | 5.65 | 5.65
1234 | 20 mm PVC couplers | each | 2 | 3.5 | 7
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 8 | 0.4 | 3.2
2920 | Washers | each | 4 | 0.17 | 0.68
1306 | 75 mm X 75 mm X 60 mm deep metal box | each | 1 | 20 | 20
1322 | 3 mm thick phenolic laminated sheet | sqcm | 72 | 0.1 | 7.2
1239 | 20 mm PVC junction box, one way | each | 1 | 15.45 | 15.45
1431 | S.P. 5/6 amps, one way switch, piano type ISI marked | each | 1 | 13.3 | 13.3
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 295.73
| Cartage @ 1 % of A1 |  |  |  | 2.9573
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 620.6873
| OVERHEADS & PROFIT @ 15 % |  |  |  | 93.1
| TOTAL |  |  |  | 713.7873
| Rate per point |  |  |  | 713.7873
| Say |  |  |  | 714
714
Analysis of rate
1.9 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required
|  |  | DSR | Rate Rs. | 719
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 13.15 | 11.1 | 145.97
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%) = 13.15m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 4.73 | 11.81 | 55.86
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
1229 | 20 mm PVC bends | each | 1 | 5.65 | 5.65
1234 | 20 mm PVC couplers | each | 2 | 3.5 | 7
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 8 | 0.4 | 3.2
2920 | Washers | each | 4 | 0.17 | 0.68
1306 | 75 mm X 75 mm X 60 mm deep metal box | each | 1 | 20 | 20
1322 | 3 mm thick phenolic laminated sheet | sqcm | 72 | 0.1 | 7.2
1239 | 20 mm PVC junction box, one way | each | 1 | 15.45 | 15.45
1432 | S.P. 5/6 amps, two way switch, piano type ISI marked | each | 1 | 17.37 | 17.37
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 299.8
| Cartage @ 1 % of A1 |  |  |  | 2.998
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 624.798
| OVERHEADS & PROFIT @ 15 % |  |  |  | 93.72
| TOTAL |  |  |  | 718.518
| Rate per point |  |  |  | 718.518
| Say |  |  |  | 719
719
Analysis of rate
1.10 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.10.1 | Group A |  | DSR | Rate Rs. | 548
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 7.88 | 11.1 | 87.47
= 2x3+1x1.5= 7.5 + 0.38 (wastage @ 5%) = 7.88 m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 2.63 | 11.81 | 31.06
= 2.5 + 0.13 (wastage @ 5%) = 2.63 m
1229 | 20 mm PVC bends | each | 1 | 5.65 | 5.65
1234 | 20 mm PVC couplers | each | 0 | 3.5 | 0
1218 | 20 mm iron staples/ saddles/ screws | each | 4 | 1.6 | 6.4
1239 | 20 mm PVC junction box, one way | each | 1 | 15.45 | 15.45
1300 | Modular GI box for 2 module | each | 0.5 | 28 | 14
1421 | Modular base & cover plate for 2 module | each | 0.5 | 39.6 | 19.8
1402 | S.P. 5/6 amps, one way modular switch, ISI marked | each | 1 | 48 | 48
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 233.45
| Cartage @ 1 % of A1 |  |  |  | 2.3345
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 476.2845
| OVERHEADS & PROFIT @ 15 % |  |  |  | 71.44
| TOTAL |  |  |  | 547.7245
| Rate per point |  |  |  | 547.7245
| Say |  |  |  | 548
548
Analysis of rate
1.10 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.10.2 | Group B |  | DSR | Rate Rs. | 615
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 10.5 | 11.1 | 116.55
= 2x4+1x2 = 10 + 0.50 (wastage @ 5%) = 10.5m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 3.68 | 11.81 | 43.46
= 3.5 + 0.18 (wastage @ 5%) = 3.68m
1229 | 20 mm PVC bends | each | 1 | 5.65 | 5.65
1234 | 20 mm PVC couplers | each | 2 | 3.5 | 7
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
1239 | 20 mm PVC junction box, one way | each | 1 | 15.45 | 15.45
1300 | Modular GI box for 2 module | each | 0.5 | 28 | 14
1421 | Modular base & cover plate for 2 module | each | 0.5 | 39.6 | 19.8
1402 | S.P. 5/6 amps, one way modular switch, ISI marked | each | 1 | 48 | 48
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 291.33
| Cartage @ 1 % of A1 |  |  |  | 2.9133
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 534.7433
| OVERHEADS & PROFIT @ 15 % |  |  |  | 80.21
| TOTAL |  |  |  | 614.9533
| Rate per point |  |  |  | 614.9533
| Say |  |  |  | 615
615
Analysis of rate
1.10 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.10.3 | Group C |  | DSR | Rate Rs. | 757
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 13.15 | 11.1 | 145.97
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%) = 13.15m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 4.73 | 11.81 | 55.86
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
1229 | 20 mm PVC bends | each | 1 | 5.65 | 5.65
1234 | 20 mm PVC couplers | each | 2 | 3.5 | 7
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
1239 | 20 mm PVC junction box, one way | each | 1 | 15.45 | 15.45
1300 | Modular GI box for 2 module | each | 0.5 | 28 | 14
1421 | Modular base & cover plate for 2 module | each | 0.5 | 39.6 | 19.8
1402 | S.P. 5/6 amps, one way modular switch, ISI marked | each | 1 | 48 | 48
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 333.15
| Cartage @ 1 % of A1 |  |  |  | 3.3315
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 658.4815
| OVERHEADS & PROFIT @ 15 % |  |  |  | 98.77
| TOTAL |  |  |  | 757.2515
| Rate per point |  |  |  | 757.2515
| Say |  |  |  | 757
757
Analysis of rate
1.11 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
|  |  | DSR | Rate Rs. | 809
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 13.15 | 11.1 | 145.97
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%) = 13.15m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 4.73 | 11.81 | 55.86
= 4.5 + 0.23 (wastage @ 5%) = 4.73m
1229 | 20 mm PVC bends | each | 1 | 5.65 | 5.65
1234 | 20 mm PVC couplers | each | 2 | 3.5 | 7
1218 | 20 mm iron staples/ saddles/ screws | each | 9 | 1.6 | 14.4
1239 | 20 mm PVC junction box, one way | each | 1 | 15.45 | 15.45
1240 | 20 mm PVC junction box, two way | each | 2 | 15.99 | 31.98
1300 | Modular GI box for 2 module | each | 0.5 | 28 | 14
1421 | Modular base & cover plate for 2 module | each | 0.5 | 39.6 | 19.8
1403 | S.P. 5/6 amps, two way modular switch, ISI marked | each | 1 | 60.8 | 60.8
2857 | PVC fastener 40mm long | each | 9 | 0.28 | 2.52
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 377.93
| Cartage @ 1 % of A1 |  |  |  | 3.7793
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1010 | Mason, Grade 2 | day | 0.1 | 407 | 40.7
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 703.7093
| OVERHEADS & PROFIT @ 15 % |  |  |  | 105.56
| TOTAL |  |  |  | 809.2693
| Rate per point |  |  |  | 809.2693
| Say |  |  |  | 809
809
Analysis of rate
1.12 | Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit along with 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required.
|  |  | DSR | Rate Rs. | 168
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 26.18 | 4164.71
= 50.5x3=151.5+7.58(Wastage @ 5%)=159.08m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 52.5 | 11.81 | 620.03
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1229 | 20 mm PVC bends | each | 4 | 5.65 | 22.6
1234 | 20 mm PVC couplers | each | 15 | 3.5 | 52.5
1218 | 20 mm iron staples/ saddles/ screws | each | 85 | 1.6 | 136
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 5024.14
| Cartage @ 1 % of A1 |  |  |  | 50.2414
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 7285.6314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1092.84
| TOTAL |  |  |  | 8378.4714
| Rate per meter |  |  |  | 167.5694
| Say |  |  |  | 168
168
Analysis of rate
1.13 | Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit along with 2 Nos 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required.
|  |  | DSR | Rate Rs. | 281
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 26.18 | 8329.17
=50.5x6=303.0+15.15(Wastage @ 5%)=318.15m
1225 | 25 mm dia. ISI marked, PVC conduit | metre | 52.5 | 20.32 | 1066.8
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1230 | 25 mm PVC bends | each | 4 | 7.7 | 30.8
1235 | 25 mm PVC couplers | each | 15 | 5.24 | 78.6
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 9719.82
| Cartage @ 1 % of A1 |  |  |  | 97.1982
LABOUR
1001 | Wireman | day | 2.25 | 447 | 1005.75
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 12232.0182
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1834.8
| TOTAL |  |  |  | 14066.8182
| Rate per meter |  |  |  | 281.3364
| Say |  |  |  | 281
281
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.1 | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire |  | DSR | Rate Rs. | 112
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 11.1 | 1765.79
= 50.5x3=151.5+7.58(Wastage @ 5%)=159.08m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 52.5 | 11.81 | 620.03
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1229 | 20 mm PVC bends | each | 4 | 5.65 | 22.6
1234 | 20 mm PVC couplers | each | 15 | 3.5 | 52.5
1218 | 20 mm iron staples/ saddles/ screws | each | 85 | 1.6 | 136
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 2625.22
| Cartage @ 1 % of A1 |  |  |  | 26.2522
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 4862.7222
| OVERHEADS & PROFIT @ 15 % |  |  |  | 729.41
| TOTAL |  |  |  | 5592.1322
| Rate per meter |  |  |  | 111.8426
| Say |  |  |  | 112
112
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.2 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire |  | DSR | Rate Rs. | 137
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 17.84 | 2837.99
= 50.5x3=151.5+7.58(Wastage @ 5%)=159.08m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 52.5 | 11.81 | 620.03
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1229 | 20 mm PVC bends | each | 4 | 5.65 | 22.6
1234 | 20 mm PVC couplers | each | 15 | 3.5 | 52.5
1218 | 20 mm iron staples/ saddles/ screws | each | 85 | 1.6 | 136
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 3697.42
| Cartage @ 1 % of A1 |  |  |  | 36.9742
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 5945.6442
| OVERHEADS & PROFIT @ 15 % |  |  |  | 891.85
| TOTAL |  |  |  | 6837.4942
| Rate per meter |  |  |  | 136.7499
| Say |  |  |  | 137
137
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.3 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire |  | DSR | Rate Rs. | 168
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 26.18 | 4164.71
= 50.5x3=151.5+7.58(Wastage @ 5%)=159.08m
1224 | 20 mm dia. ISI marked, PVC conduit | metre | 52.5 | 11.81 | 620.03
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1229 | 20 mm PVC bends | each | 4 | 5.65 | 22.6
1234 | 20 mm PVC couplers | each | 15 | 3.5 | 52.5
1218 | 20 mm iron staples/ saddles/ screws | each | 85 | 1.6 | 136
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 5024.14
| Cartage @ 1 % of A1 |  |  |  | 50.2414
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 7285.6314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1092.84
| TOTAL |  |  |  | 8378.4714
| Rate per meter |  |  |  | 167.5694
| Say |  |  |  | 168
168
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.4 | 2 X 6 sq. mm + 1 X 6 sq. mm earth wire |  | DSR | Rate Rs. | 227
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 38.87 | 6183.44
= 50.5x3=151.5+7.58(Wastage @ 5%)=159.08m
1225 | 25 mm dia. ISI marked, PVC conduit | metre | 52.5 | 20.32 | 1066.8
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1230 | 25 mm PVC bends | each | 4 | 7.7 | 30.8
1235 | 25 mm PVC couplers | each | 15 | 5.24 | 78.6
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 7574.09
| Cartage @ 1 % of A1 |  |  |  | 75.7409
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 9861.0809
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1479.16
| TOTAL |  |  |  | 11340.2409
| Rate per meter |  |  |  | 226.8048
| Say |  |  |  | 227
227
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.5 | 2 X 10 sq. mm + 1 X 10 sq. mm earth wire |  | DSR | Rate Rs. | 299
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1105 | 10 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5x2=101.0+5.05(Wastage @ 5%)=106.05m | metre | 106.05 | 66.43 | 7044.9
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5+2.53(Wastage @ 5%)=53.03m | metre | 53.03 | 38.87 | 2061.28
1225 | 25 mm dia. ISI marked, PVC conduit | metre | 52.5 | 20.32 | 1066.8
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1230 | 25 mm PVC bends | each | 4 | 7.7 | 30.8
1235 | 25 mm PVC couplers | each | 15 | 5.24 | 78.6
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 10496.83
| Cartage @ 1 % of A1 |  |  |  | 104.9683
LABOUR
1001 | Wireman | day | 2.25 | 447 | 1005.75
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 13016.7983
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1952.52
| TOTAL |  |  |  | 14969.3183
| Rate per meter |  |  |  | 299.3864
| Say |  |  |  | 299
299
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.6 | 2 X 16 sq. mm + 1 X 16 sq. mm earth wire |  | DSR | Rate Rs. | 408
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1106 | 16 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5x2=101.0+5.05(Wastage @ 5%)=106.05m | metre | 106.05 | 102.36 | 10855.28
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5+2.53(Wastage @ 5%)=53.03m | metre | 53.03 | 38.87 | 2061.28
1226 | 32 mm dia. ISI marked, PVC conduit | metre | 52.5 | 33.59 | 1763.48
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1231 | 32 mm PVC bends | each | 4 | 13.16 | 52.64
1236 | 32 mm PVC couplers | each | 15 | 8.55 | 128.25
1220 | 32 mm iron staples/ saddles/ screws | each | 85 | 3.34 | 283.9
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 15173.13
| Cartage @ 1 % of A1 |  |  |  | 151.7313
LABOUR
1001 | Wireman | day | 2.25 | 447 | 1005.75
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 17739.8613
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2660.98
| TOTAL |  |  |  | 20400.8413
| Rate per meter |  |  |  | 408.0168
| Say |  |  |  | 408
408
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.7 | 4 X 2.5 sq. mm + 2 X 2.5 sq. mm earth wire |  | DSR | Rate Rs. | 215
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 17.84 | 5675.8
=50.5x6=303.0+15.15(Wastage @ 5%)=318.15m
1225 | 25 mm dia. ISI marked, PVC conduit | metre | 52.5 | 20.32 | 1066.8
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1230 | 25 mm PVC bends | each | 4 | 7.7 | 30.8
1235 | 25 mm PVC couplers | each | 15 | 5.24 | 78.6
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 7066.45
| Cartage @ 1 % of A1 |  |  |  | 70.6645
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 9348.3645
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1402.25
| TOTAL |  |  |  | 10750.6145
| Rate per meter |  |  |  | 215.0123
| Say |  |  |  | 215
215
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.8 | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire |  | DSR | Rate Rs. | 281
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 26.18 | 8329.17
=50.5x6=303.0+15.15(Wastage @ 5%)=318.15m
1225 | 25 mm dia. ISI marked, PVC conduit | metre | 52.5 | 20.32 | 1066.8
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1230 | 25 mm PVC bends | each | 4 | 7.7 | 30.8
1235 | 25 mm PVC couplers | each | 15 | 5.24 | 78.6
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 9719.82
| Cartage @ 1 % of A1 |  |  |  | 97.1982
LABOUR
1001 | Wireman | day | 2.25 | 447 | 1005.75
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 12232.0182
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1834.8
| TOTAL |  |  |  | 14066.8182
| Rate per meter |  |  |  | 281.3364
| Say |  |  |  | 281
281
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.9 | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire |  | DSR | Rate Rs. | 395
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 38.87 | 12366.49
=50.5x6=303.0+15.15(Wastage @ 5%)=318.15m
1226 | 32 mm dia. ISI marked, PVC conduit | metre | 52.5 | 33.59 | 1763.48
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1231 | 32 mm PVC bends | each | 4 | 13.16 | 52.64
1236 | 32 mm PVC couplers | each | 15 | 8.55 | 128.25
1220 | 32 mm iron staples/ saddles/ screws | each | 85 | 3.34 | 283.9
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 14623.06
| Cartage @ 1 % of A1 |  |  |  | 146.2306
LABOUR
1001 | Wireman | day | 2.25 | 447 | 1005.75
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 17184.2906
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2577.64
| TOTAL |  |  |  | 19761.9306
| Rate per meter |  |  |  | 395.2386
| Say |  |  |  | 395
395
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.10 | 4 X 10 sq. mm + 2 X 10 sq. mm earth wire |  | DSR | Rate Rs. | 536
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1105 | 10 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable=50.5x4=202.0+10.10(Wastage @ 5%)=212.10m | metre | 212.1 | 66.43 | 14089.8
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5x2=101.0+5.05(Wastage @ 5%)=106.05m | metre | 106.05 | 38.87 | 4122.16
1226 | 32 mm dia. ISI marked, PVC conduit | metre | 52.5 | 33.59 | 1763.48
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1231 | 32 mm PVC bends | each | 4 | 13.16 | 52.64
1236 | 32 mm PVC couplers | each | 15 | 8.55 | 128.25
1220 | 32 mm iron staples/ saddles/ screws | each | 85 | 3.34 | 283.9
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 20468.53
| Cartage @ 1 % of A1 |  |  |  | 204.6853
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 23291.9653
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3493.79
| TOTAL |  |  |  | 26785.7553
| Rate per meter |  |  |  | 535.7151
| Say |  |  |  | 536
536
Analysis of rate
1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
1.14.11 | 4 X 16 sq. mm + 2 X 16 sq. mm earth wire |  | DSR | Rate Rs. | 733
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1106 | 16 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable=50.5x4=202.0+10.10(Wastage @ 5%)=212.10m | metre | 212.1 | 102.36 | 21710.56
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable= 50.5x2=101.0+5.05(Wastage @ 5%)=106.05m | metre | 106.05 | 38.87 | 4122.16
1227 | 40 mm dia. ISI marked, PVC conduit | metre | 52.5 | 47.37 | 2486.93
= 50.0 + 2.5 (Wastage @ 5%) = 52.5m
1232 | 40 mm PVC bends | each | 4 | 20.98 | 83.92
1237 | 40 mm PVC couplers | each | 15 | 10.44 | 156.6
1221 | 40 mm iron staples/ saddles/ screws | each | 85 | 4.31 | 366.35
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 28954.82
| Cartage @ 1 % of A1 |  |  |  | 289.5482
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 31863.1182
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4779.47
| TOTAL |  |  |  | 36642.5882
| Rate per meter |  |  |  | 732.8518
| Say |  |  |  | 733
733
Analysis of rate
1.15 | Rewiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable and 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed steel conduit including dismantling as required.
1.15.1 | Group A |  | DSR | Rate Rs. | 290
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 7.88 | 11.1 | 87.47
= 2x3+1x1.5= 7.5 + 0.38 (wastage @ 5%) = 7.88 m
2859 | Rubber/ PVC bushes | each | 1 | 0.5 | 0.5
| Total cost of materials |  |  |  | 87.97
| Cartage @ 1 % of A1 |  |  |  | 0.8797
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 251.8497
| OVERHEADS & PROFIT @ 15 % |  |  |  | 37.78
| TOTAL |  |  |  | 289.6297
| Rate per point |  |  |  | 289.6297
| Say |  |  |  | 290
290
Analysis of rate
1.15 | Rewiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable and 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed steel conduit including dismantling as required.
1.15.2 | Group B |  | DSR | Rate Rs. | 323
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 10.5 | 11.1 | 116.55
= 2x4+1x2 = 10 + 0.50 (wastage @ 5%) = 10.5m
2859 | Rubber/ PVC bushes | each | 1 | 0.5 | 0.5
| Total cost of materials |  |  |  | 117.05
| Cartage @ 1 % of A1 |  |  |  | 1.1705
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 281.2205
| OVERHEADS & PROFIT @ 15 % |  |  |  | 42.18
| TOTAL |  |  |  | 323.4005
| Rate per point |  |  |  | 323.4005
| Say |  |  |  | 323
323
Analysis of rate
1.15 | Rewiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable and 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed steel conduit including dismantling as required.
1.15.3 | Group C |  | DSR | Rate Rs. | 452
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 13.15 | 11.1 | 145.97
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%) = 13.15m
2859 | Rubber/ PVC bushes | each | 2 | 0.5 | 1
| Total cost of materials |  |  |  | 146.97
| Cartage @ 1 % of A1 |  |  |  | 1.4697
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 392.9397
| OVERHEADS & PROFIT @ 15 % |  |  |  | 58.94
| TOTAL |  |  |  | 451.8797
| Rate per point |  |  |  | 451.8797
| Say |  |  |  | 452
452
Analysis of rate
1.16 | Rewiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable and 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed steel conduit including dismantling as required.
|  |  | DSR | Rate Rs. | 452
COST FOR 1 POINT
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 13.15 | 11.1 | 145.97
= 2x5+1x2.5 = 12.5 + 0.65 (wastage @ 5%) = 13.15m
2859 | Rubber/ PVC bushes | each | 2 | 0.5 | 1
| Total cost of materials |  |  |  | 146.97
| Cartage @ 1 % of A1 |  |  |  | 1.4697
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 392.9397
| OVERHEADS & PROFIT @ 15 % |  |  |  | 58.94
| TOTAL |  |  |  | 451.8797
| Rate per point |  |  |  | 451.8797
| Say |  |  |  | 452
452
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.1 | 1 x 1.5 sq. mm |  | DSR | Rate Rs. | 23
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 53.03 | 11.1 | 588.63
=50.5x1=50.5+2.53 (Wastage @ 5%)=53.03m
| Total cost of materials |  |  |  | 588.63
| Cartage @ 1 % of A1 |  |  |  | 5.8863
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 1002.0163
| OVERHEADS & PROFIT @ 15 % |  |  |  | 150.3
| TOTAL |  |  |  | 1152.3163
| Rate per meter |  |  |  | 23.0463
| Say |  |  |  | 23
23
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.2 | 2 x 1.5 sq. mm |  | DSR | Rate Rs. | 37
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 106.05 | 11.1 | 1177.16
=50.5x2=101+5.05 (Wastage @ 5%) = 106.05m
| Total cost of materials |  |  |  | 1177.16
| Cartage @ 1 % of A1 |  |  |  | 11.7716
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 1596.4316
| OVERHEADS & PROFIT @ 15 % |  |  |  | 239.46
| TOTAL |  |  |  | 1835.8916
| Rate per meter |  |  |  | 36.7178
| Say |  |  |  | 37
37
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.3 | 3 x 1.5 sq. mm |  | DSR | Rate Rs. | 50
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 11.1 | 1765.79
=50.5x3=151.5+7.58 (Wastage @ 5%)=159.08m
| Total cost of materials |  |  |  | 1765.79
| Cartage @ 1 % of A1 |  |  |  | 17.6579
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 2190.9479
| OVERHEADS & PROFIT @ 15 % |  |  |  | 328.64
| TOTAL |  |  |  | 2519.5879
| Rate per meter |  |  |  | 50.3918
| Say |  |  |  | 50
50
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.4 | 4 x 1.5 sq. mm |  | DSR | Rate Rs. | 64
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 212.1 | 11.1 | 2354.31
=50.5x4 = 202 + 10.1 (Wastage @ 5%) = 212.1m
| Total cost of materials |  |  |  | 2354.31
| Cartage @ 1 % of A1 |  |  |  | 23.5431
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 2785.3531
| OVERHEADS & PROFIT @ 15 % |  |  |  | 417.8
| TOTAL |  |  |  | 3203.1531
| Rate per meter |  |  |  | 64.0631
| Say |  |  |  | 64
64
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.5 | 5 x 1.5 sq. mm |  | DSR | Rate Rs. | 82
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 265.13 | 11.1 | 2942.94
=50.5x5=252.5+12.63 (Wastage @ 5%)=265.13m
| Total cost of materials |  |  |  | 2942.94
| Cartage @ 1 % of A1 |  |  |  | 29.4294
LABOUR
1001 | Wireman | day | 0.75 | 447 | 335.25
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 3583.6194
| OVERHEADS & PROFIT @ 15 % |  |  |  | 537.54
| TOTAL |  |  |  | 4121.1594
| Rate per meter |  |  |  | 82.4232
| Say |  |  |  | 82
82
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.6 | 6 x 1.5 sq. mm |  | DSR | Rate Rs. | 96
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 11.1 | 3531.47
= 50.5x6 = 303 + 15.15 (Wastage @ 5%) = 318.15m
| Total cost of materials |  |  |  | 3531.47
| Cartage @ 1 % of A1 |  |  |  | 35.3147
LABOUR
1001 | Wireman | day | 0.75 | 447 | 335.25
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 4178.0347
| OVERHEADS & PROFIT @ 15 % |  |  |  | 626.71
| TOTAL |  |  |  | 4804.7447
| Rate per meter |  |  |  | 96.0949
| Say |  |  |  | 96
96
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.7 | 7 x 1.5 sq. mm |  | DSR | Rate Rs. | 114
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 371.18 | 11.1 | 4120.1
= 50.5x7 = 353.5 + 17.68 (Wastage @ 5%) = 371.18m
| Total cost of materials |  |  |  | 4120.1
| Cartage @ 1 % of A1 |  |  |  | 41.201
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 4976.301
| OVERHEADS & PROFIT @ 15 % |  |  |  | 746.45
| TOTAL |  |  |  | 5722.751
| Rate per meter |  |  |  | 114.455
| Say |  |  |  | 114
114
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.8 | 8 x 1.5 sq. mm |  | DSR | Rate Rs. | 128
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 424.2 | 11.1 | 4708.62
= 50.5x8 = 404 + 20.2 (Wastage @ 5%) = 424.2m
| Total cost of materials |  |  |  | 4708.62
| Cartage @ 1 % of A1 |  |  |  | 47.0862
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 5570.7062
| OVERHEADS & PROFIT @ 15 % |  |  |  | 835.61
| TOTAL |  |  |  | 6406.3162
| Rate per meter |  |  |  | 128.1263
| Say |  |  |  | 128
128
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.9 | 9 x 1.5 sq. mm |  | DSR | Rate Rs. | 151
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 477.23 | 11.1 | 5297.25
= 50.5x9 = 454.5 + 22.73 (Wastage @ 5%) = 477.23m
| Total cost of materials |  |  |  | 5297.25
| Cartage @ 1 % of A1 |  |  |  | 52.9725
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 1.5 | 368 | 552
| TOTAL |  |  |  | 6572.7225
| OVERHEADS & PROFIT @ 15 % |  |  |  | 985.91
| TOTAL |  |  |  | 7558.6325
| Rate per meter |  |  |  | 151.1727
| Say |  |  |  | 151
151
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.10 | 10 x 1.5 sq. mm |  | DSR | Rate Rs. | 165
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 530.25 | 11.1 | 5885.78
= 50.5x10 = 505 + 25.25 (Wastage @ 5%) = 530.25m
| Total cost of materials |  |  |  | 5885.78
| Cartage @ 1 % of A1 |  |  |  | 58.8578
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 1.5 | 368 | 552
| TOTAL |  |  |  | 7167.1378
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1075.07
| TOTAL |  |  |  | 8242.2078
| Rate per meter |  |  |  | 164.8442
| Say |  |  |  | 165
165
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.11 | 2 x 2.5 sq. mm |  | DSR | Rate Rs. | 53
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 106.05 | 17.84 | 1891.93
=50.5x2=101+5.05 (Wastage @ 5%) = 106.05m
| Total cost of materials |  |  |  | 1891.93
| Cartage @ 1 % of A1 |  |  |  | 18.9193
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 2318.3493
| OVERHEADS & PROFIT @ 15 % |  |  |  | 347.75
| TOTAL |  |  |  | 2666.0993
| Rate per meter |  |  |  | 53.322
| Say |  |  |  | 53
53
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.12 | 3 x 2.5 sq. mm |  | DSR | Rate Rs. | 75
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 17.84 | 2837.99
=50.5x3=151.5+7.58 (Wastage @ 5%)=159.08m
| Total cost of materials |  |  |  | 2837.99
| Cartage @ 1 % of A1 |  |  |  | 28.3799
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 3273.8699
| OVERHEADS & PROFIT @ 15 % |  |  |  | 491.08
| TOTAL |  |  |  | 3764.9499
| Rate per meter |  |  |  | 75.299
| Say |  |  |  | 75
75
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.13 | 4 x 2.5 sq. mm |  | DSR | Rate Rs. | 97
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 212.1 | 17.84 | 3783.86
=50.5x4 = 202 + 10.1 (Wastage @ 5%) = 212.1m
| Total cost of materials |  |  |  | 3783.86
| Cartage @ 1 % of A1 |  |  |  | 37.8386
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 4229.1986
| OVERHEADS & PROFIT @ 15 % |  |  |  | 634.38
| TOTAL |  |  |  | 4863.5786
| Rate per meter |  |  |  | 97.2716
| Say |  |  |  | 97
97
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.14 | 5 x 2.5 sq. mm |  | DSR | Rate Rs. | 124
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 265.13 | 17.84 | 4729.92
=50.5x5=252.5+12.63 (Wastage @ 5%)=265.13m
| Total cost of materials |  |  |  | 4729.92
| Cartage @ 1 % of A1 |  |  |  | 47.2992
LABOUR
1001 | Wireman | day | 0.75 | 447 | 335.25
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 5388.4692
| OVERHEADS & PROFIT @ 15 % |  |  |  | 808.27
| TOTAL |  |  |  | 6196.7392
| Rate per meter |  |  |  | 123.9348
| Say |  |  |  | 124
124
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.15 | 6 x 2.5 sq. mm |  | DSR | Rate Rs. | 146
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 17.84 | 5675.8
= 50.5x6 = 303 + 15.15 (Wastage @ 5%) = 318.15m
| Total cost of materials |  |  |  | 5675.8
| Cartage @ 1 % of A1 |  |  |  | 56.758
LABOUR
1001 | Wireman | day | 0.75 | 447 | 335.25
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 6343.808
| OVERHEADS & PROFIT @ 15 % |  |  |  | 951.57
| TOTAL |  |  |  | 7295.378
| Rate per meter |  |  |  | 145.9076
| Say |  |  |  | 146
146
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.16 | 7 x 2.5 sq. mm |  | DSR | Rate Rs. | 173
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 371.18 | 17.84 | 6621.85
= 50.5x7 = 353.5 + 17.68 (Wastage @ 5%) = 371.18m
| Total cost of materials |  |  |  | 6621.85
| Cartage @ 1 % of A1 |  |  |  | 66.2185
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 7503.0685
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1125.46
| TOTAL |  |  |  | 8628.5285
| Rate per meter |  |  |  | 172.5706
| Say |  |  |  | 173
173
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.17 | 8 x 2.5 sq. mm |  | DSR | Rate Rs. | 195
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 424.2 | 17.84 | 7567.73
= 50.5x8 = 404 + 20.2 (Wastage @ 5%) = 424.2m
| Total cost of materials |  |  |  | 7567.73
| Cartage @ 1 % of A1 |  |  |  | 75.6773
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 8458.4073
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1268.76
| TOTAL |  |  |  | 9727.1673
| Rate per meter |  |  |  | 194.5433
| Say |  |  |  | 195
195
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.18 | 9 x 2.5 sq. mm |  | DSR | Rate Rs. | 226
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 477.23 | 17.84 | 8513.78
= 50.5x9 = 454.5 + 22.73 (Wastage @ 5%) = 477.23m
| Total cost of materials |  |  |  | 8513.78
| Cartage @ 1 % of A1 |  |  |  | 85.1378
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 1.5 | 368 | 552
| TOTAL |  |  |  | 9821.4178
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1473.21
| TOTAL |  |  |  | 11294.6278
| Rate per meter |  |  |  | 225.8926
| Say |  |  |  | 226
226
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.19 | 10 x 2.5 sq. mm |  | DSR | Rate Rs. | 248
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1102 | 2.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 530.25 | 17.84 | 9459.66
= 50.5x10 = 505 + 25.25 (Wastage @ 5%) = 530.25m
| Total cost of materials |  |  |  | 9459.66
| Cartage @ 1 % of A1 |  |  |  | 94.5966
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 1.5 | 368 | 552
| TOTAL |  |  |  | 10776.7566
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1616.51
| TOTAL |  |  |  | 12393.2666
| Rate per meter |  |  |  | 247.8653
| Say |  |  |  | 248
248
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.20 | 2 x 4 sq. mm |  | DSR | Rate Rs. | 79
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 106.05 | 26.18 | 2776.39
=50.5x2=101+5.05 (Wastage @ 5%) = 106.05m
| Total cost of materials |  |  |  | 2776.39
| Cartage @ 1 % of A1 |  |  |  | 27.7639
LABOUR
1001 | Wireman | day | 0.75 | 447 | 335.25
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 3415.4039
| OVERHEADS & PROFIT @ 15 % |  |  |  | 512.31
| TOTAL |  |  |  | 3927.7139
| Rate per meter |  |  |  | 78.5543
| Say |  |  |  | 79
79
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.21 | 3 x 4 sq. mm |  | DSR | Rate Rs. | 111
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 26.18 | 4164.71
=50.5x3=151.5+7.58 (Wastage @ 5%)=159.08m
| Total cost of materials |  |  |  | 4164.71
| Cartage @ 1 % of A1 |  |  |  | 41.6471
LABOUR
1001 | Wireman | day | 0.75 | 447 | 335.25
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 4817.6071
| OVERHEADS & PROFIT @ 15 % |  |  |  | 722.64
| TOTAL |  |  |  | 5540.2471
| Rate per meter |  |  |  | 110.8049
| Say |  |  |  | 111
111
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.22 | 4 x 4 sq. mm |  | DSR | Rate Rs. | 148
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 212.1 | 26.18 | 5552.78
=50.5x4 = 202 + 10.1 (Wastage @ 5%) = 212.1m
| Total cost of materials |  |  |  | 5552.78
| Cartage @ 1 % of A1 |  |  |  | 55.5278
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 6423.3078
| OVERHEADS & PROFIT @ 15 % |  |  |  | 963.5
| TOTAL |  |  |  | 7386.8078
| Rate per meter |  |  |  | 147.7362
| Say |  |  |  | 148
148
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.23 | 5 x 4 sq. mm |  | DSR | Rate Rs. | 182
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 265.13 | 26.18 | 6941.1
=50.5x5=252.5+12.63 (Wastage @ 5%)=265.13m
| Total cost of materials |  |  |  | 6941.1
| Cartage @ 1 % of A1 |  |  |  | 69.411
LABOUR
1001 | Wireman | day | 1.1 | 447 | 491.7
1007 | Khallasi | day | 1.1 | 368 | 404.8
| TOTAL |  |  |  | 7907.011
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1186.05
| TOTAL |  |  |  | 9093.061
| Rate per meter |  |  |  | 181.8612
| Say |  |  |  | 182
182
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.24 | 6 x 4 sq. mm |  | DSR | Rate Rs. | 214
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 26.18 | 8329.17
= 50.5x6 = 303 + 15.15 (Wastage @ 5%) = 318.15m
| Total cost of materials |  |  |  | 8329.17
| Cartage @ 1 % of A1 |  |  |  | 83.2917
LABOUR
1001 | Wireman | day | 1.1 | 447 | 491.7
1007 | Khallasi | day | 1.1 | 368 | 404.8
| TOTAL |  |  |  | 9308.9617
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1396.34
| TOTAL |  |  |  | 10705.3017
| Rate per meter |  |  |  | 214.106
| Say |  |  |  | 214
214
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.25 | 7 x 4 sq. mm |  | DSR | Rate Rs. | 247
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 371.18 | 26.18 | 9717.49
= 50.5x7 = 353.5 + 17.68 (Wastage @ 5%) = 371.18m
| Total cost of materials |  |  |  | 9717.49
| Cartage @ 1 % of A1 |  |  |  | 97.1749
LABOUR
1001 | Wireman | day | 1.15 | 447 | 514.05
1007 | Khallasi | day | 1.15 | 368 | 423.2
| TOTAL |  |  |  | 10751.9149
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1612.79
| TOTAL |  |  |  | 12364.7049
| Rate per meter |  |  |  | 247.2941
| Say |  |  |  | 247
247
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.26 | 8 x 4 sq. mm |  | DSR | Rate Rs. | 280
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 424.2 | 26.18 | 11105.56
= 50.5x8 = 404 + 20.2 (Wastage @ 5%) = 424.2m
| Total cost of materials |  |  |  | 11105.56
| Cartage @ 1 % of A1 |  |  |  | 111.0556
LABOUR
1001 | Wireman | day | 1.15 | 447 | 514.05
1007 | Khallasi | day | 1.15 | 368 | 423.2
| TOTAL |  |  |  | 12153.8656
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1823.08
| TOTAL |  |  |  | 13976.9456
| Rate per meter |  |  |  | 279.5389
| Say |  |  |  | 280
280
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.27 | 9 x 4 sq. mm |  | DSR | Rate Rs. | 314
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 477.23 | 26.18 | 12493.88
= 50.5x9 = 454.5 + 22.73 (Wastage @ 5%) = 477.23m
| Total cost of materials |  |  |  | 12493.88
| Cartage @ 1 % of A1 |  |  |  | 124.9388
LABOUR
1001 | Wireman | day | 1.25 | 447 | 558.75
1007 | Khallasi | day | 1.25 | 368 | 460
| TOTAL |  |  |  | 13637.5688
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2045.64
| TOTAL |  |  |  | 15683.2088
| Rate per meter |  |  |  | 313.6642
| Say |  |  |  | 314
314
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.28 | 10 x 4 sq. mm |  | DSR | Rate Rs. | 351
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1103 | 4.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 530.25 | 26.18 | 13881.95
= 50.5x10 = 505 + 25.25 (Wastage @ 5%) = 530.25m
| Total cost of materials |  |  |  | 13881.95
| Cartage @ 1 % of A1 |  |  |  | 138.8195
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 1.5 | 368 | 552
| TOTAL |  |  |  | 15243.2695
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2286.49
| TOTAL |  |  |  | 17529.7595
| Rate per meter |  |  |  | 350.5952
| Say |  |  |  | 351
351
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.29 | 2 x 6 sq. mm |  | DSR | Rate Rs. | 115
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 106.05 | 38.87 | 4122.16
=50.5x2=101+5.05 (Wastage @ 5%) = 106.05m
| Total cost of materials |  |  |  | 4122.16
| Cartage @ 1 % of A1 |  |  |  | 41.2216
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 4978.3816
| OVERHEADS & PROFIT @ 15 % |  |  |  | 746.76
| TOTAL |  |  |  | 5725.1416
| Rate per meter |  |  |  | 114.5028
| Say |  |  |  | 115
115
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.30 | 3 x 6 sq. mm |  | DSR | Rate Rs. | 162
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 159.08 | 38.87 | 6183.44
=50.5x3=151.5+7.58 (Wastage @ 5%)=159.08m
| Total cost of materials |  |  |  | 6183.44
| Cartage @ 1 % of A1 |  |  |  | 61.8344
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 7060.2744
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1059.04
| TOTAL |  |  |  | 8119.3144
| Rate per meter |  |  |  | 162.3863
| Say |  |  |  | 162
162
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.31 | 4 x 6 sq. mm |  | DSR | Rate Rs. | 215
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 212.1 | 38.87 | 8244.33
=50.5x4 = 202 + 10.1 (Wastage @ 5%) = 212.1m
| Total cost of materials |  |  |  | 8244.33
| Cartage @ 1 % of A1 |  |  |  | 82.4433
LABOUR
1001 | Wireman | day | 1.25 | 447 | 558.75
1007 | Khallasi | day | 1.25 | 368 | 460
| TOTAL |  |  |  | 9345.5233
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1401.83
| TOTAL |  |  |  | 10747.3533
| Rate per meter |  |  |  | 214.9471
| Say |  |  |  | 215
215
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.32 | 5 x 6 sq. mm |  | DSR | Rate Rs. | 263
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 265.13 | 38.87 | 10305.6
=50.5x5=252.5+12.63 (Wastage @ 5%)=265.13m
| Total cost of materials |  |  |  | 10305.6
| Cartage @ 1 % of A1 |  |  |  | 103.056
LABOUR
1001 | Wireman | day | 1.25 | 447 | 558.75
1007 | Khallasi | day | 1.25 | 368 | 460
| TOTAL |  |  |  | 11427.406
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1714.11
| TOTAL |  |  |  | 13141.516
| Rate per meter |  |  |  | 262.8303
| Say |  |  |  | 263
263
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.33 | 6 x 6 sq. mm |  | DSR | Rate Rs. | 320
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 318.15 | 38.87 | 12366.49
= 50.5x6 = 303 + 15.15 (Wastage @ 5%) = 318.15m
| Total cost of materials |  |  |  | 12366.49
| Cartage @ 1 % of A1 |  |  |  | 123.6649
LABOUR
1001 | Wireman | day | 1.75 | 447 | 782.25
1007 | Khallasi | day | 1.75 | 368 | 644
| TOTAL |  |  |  | 13916.4049
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2087.46
| TOTAL |  |  |  | 16003.8649
| Rate per meter |  |  |  | 320.0773
| Say |  |  |  | 320
320
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.34 | 7 x 6 sq. mm |  | DSR | Rate Rs. | 368
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 371.18 | 38.87 | 14427.77
= 50.5x7 = 353.5 + 17.68 (Wastage @ 5%) = 371.18m
| Total cost of materials |  |  |  | 14427.77
| Cartage @ 1 % of A1 |  |  |  | 144.2777
LABOUR
1001 | Wireman | day | 1.75 | 447 | 782.25
1007 | Khallasi | day | 1.75 | 368 | 644
| TOTAL |  |  |  | 15998.2977
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2399.74
| TOTAL |  |  |  | 18398.0377
| Rate per meter |  |  |  | 367.9608
| Say |  |  |  | 368
368
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.35 | 8 x 6 sq. mm |  | DSR | Rate Rs. | 421
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 424.2 | 38.87 | 16488.65
= 50.5x8 = 404 + 20.2 (Wastage @ 5%) = 424.2m
| Total cost of materials |  |  |  | 16488.65
| Cartage @ 1 % of A1 |  |  |  | 164.8865
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 18283.5365
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2742.53
| TOTAL |  |  |  | 21026.0665
| Rate per meter |  |  |  | 420.5213
| Say |  |  |  | 421
421
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.36 | 9 x 6 sq. mm |  | DSR | Rate Rs. | 468
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 477.23 | 38.87 | 18549.93
= 50.5x9 = 454.5 + 22.73 (Wastage @ 5%) = 477.23m
| Total cost of materials |  |  |  | 18549.93
| Cartage @ 1 % of A1 |  |  |  | 185.4993
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 20365.4293
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3054.81
| TOTAL |  |  |  | 23420.2393
| Rate per meter |  |  |  | 468.4048
| Say |  |  |  | 468
468
Analysis of rate
1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
1.17.37 | 10 x 6 sq. mm |  | DSR | Rate Rs. | 519
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1104 | 6.0 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 530.25 | 38.87 | 20610.82
= 50.5x10 = 505 + 25.25 (Wastage @ 5%) = 530.25m
| Total cost of materials |  |  |  | 20610.82
| Cartage @ 1 % of A1 |  |  |  | 206.1082
LABOUR
1001 | Wireman | day | 2.13 | 447 | 952.11
1007 | Khallasi | day | 2.13 | 368 | 783.84
| TOTAL |  |  |  | 22552.8782
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3382.93
| TOTAL |  |  |  | 25935.8082
| Rate per meter |  |  |  | 518.7162
| Say |  |  |  | 519
519
Analysis of rate
1.18 | Supplying and drawing following pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
1.18.1 | 1 Pair |  | DSR | Rate Rs. | 15
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1111 | 1 pair, 0.5 mm dia annealed copper conductor, FRLS PVC insulated, unarmoured, telephone cable | metre | 53.03 | 4.71 | 249.77
= 50.5x1 = 50.5 + 2.53 (Wastage @ 5%) = 53.03m
| Total cost of materials |  |  |  | 249.77
| Cartage @ 1 % of A1 |  |  |  | 2.4977
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 659.7677
| OVERHEADS & PROFIT @ 15 % |  |  |  | 98.97
| TOTAL |  |  |  | 758.7377
| Rate per meter |  |  |  | 15.1748
| Say |  |  |  | 15
15
Analysis of rate
1.18 | Supplying and drawing following pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
1.18.2 | 2 Pair |  | DSR | Rate Rs. | 19
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1112 | 2 pair, 0.5 mm dia annealed copper conductor, FRLS PVC insulated, unarmoured, telephone cable | metre | 53.03 | 7.94 | 421.06
= 50.5x1 = 50.5 + 2.53 (Wastage @ 5%) = 53.03m
| Total cost of materials |  |  |  | 421.06
| Cartage @ 1 % of A1 |  |  |  | 4.2106
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 832.7706
| OVERHEADS & PROFIT @ 15 % |  |  |  | 124.92
| TOTAL |  |  |  | 957.6906
| Rate per meter |  |  |  | 19.1538
| Say |  |  |  | 19
19
Analysis of rate
1.18 | Supplying and drawing following pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
1.18.3 | 4 Pair |  | DSR | Rate Rs. | 28
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1113 | 4 pair, 0.5 mm dia annealed copper conductor, FRLS PVC insulated, unarmoured, telephone cable | metre | 53.03 | 15.3 | 811.36
= 50.5x1 = 50.5 + 2.53 (Wastage @ 5%) = 53.03m
| Total cost of materials |  |  |  | 811.36
| Cartage @ 1 % of A1 |  |  |  | 8.1136
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 1226.9736
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.05
| TOTAL |  |  |  | 1411.0236
| Rate per meter |  |  |  | 28.2205
| Say |  |  |  | 28
28
Analysis of rate
1.19 | Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required.
|  |  | DSR | Rate Rs. | 29
COST FOR 50 METRES
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1114 | Co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid protected with PVC sheath | metre | 53.03 | 15.67 | 830.98
= 50.5x1 = 50.5 + 2.53 (Wastage @ 5%) = 53.03m
| Total cost of materials |  |  |  | 830.98
| Cartage @ 1 % of A1 |  |  |  | 8.3098
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 1246.7898
| OVERHEADS & PROFIT @ 15 % |  |  |  | 187.02
| TOTAL |  |  |  | 1433.8098
| Rate per meter |  |  |  | 28.6762
| Say |  |  |  | 29
29
Analysis of rate
1.20 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
1.20.1 | 20 mm |  | DSR | Rate Rs. | 126
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
1201 | 20 mm dia. ISI marked, steel conduit = 50.0 + 2.50 (Wastage @ 5%) = 52.50m | metre | 52.5 | 60.01 | 3150.53
1206 | 20 mm inspection/ solid bends | each | 4 | 7.61 | 30.44
1211 | 20 mm sockets | each | 15 | 6.93 | 103.95
1218 | 20 mm iron staples/ saddles/ screws | each | 85 | 1.6 | 136
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | LS | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 3449.22
| Cartage @ 1 % of A1 |  |  |  | 34.4922
LABOUR
1001 | Wireman | day | 1.75 | 447 | 782.25
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 2.5 | 368 | 920
| TOTAL |  |  |  | 5493.2522
| OVERHEADS & PROFIT @ 15 % |  |  |  | 823.99
| TOTAL |  |  |  | 6317.2422
| Rate per meter |  |  |  | 126.3448
| Say |  |  |  | 126
126
Analysis of rate
1.20 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
1.20.2 | 25 mm |  | DSR | Rate Rs. | 147
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
1202 | 25 mm dia. ISI marked, steel conduit = 50.0 + 2.50 (Wastage @ 5%) = 52.50m | metre | 52.5 | 75.6 | 3969
1207 | 25 mm inspection/ solid bends | each | 4 | 13.39 | 53.56
1212 | 25 mm sockets | each | 15 | 7.56 | 113.4
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | LS | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 4350.41
| Cartage @ 1 % of A1 |  |  |  | 43.5041
LABOUR
1001 | Wireman | day | 1.75 | 447 | 782.25
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 2.5 | 368 | 920
| TOTAL |  |  |  | 6403.4541
| OVERHEADS & PROFIT @ 15 % |  |  |  | 960.52
| TOTAL |  |  |  | 7363.9741
| Rate per meter |  |  |  | 147.2795
| Say |  |  |  | 147
147
Analysis of rate
1.20 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
1.20.3 | 32 mm |  | DSR | Rate Rs. | 198
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
1203 | 32 mm dia. ISI marked, steel conduit = 50.0 + 2.50 (Wastage @ 5%) = 52.50m | metre | 52.5 | 113.4 | 5953.5
1208 | 32 mm inspection/ solid bends | each | 4 | 25.2 | 100.8
1213 | 32 mm sockets | each | 15 | 9.77 | 146.55
1220 | 32 mm iron staples/ saddles/ screws | each | 85 | 3.34 | 283.9
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | LS | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 6513.05
| Cartage @ 1 % of A1 |  |  |  | 65.1305
LABOUR
1001 | Wireman | day | 1.75 | 447 | 782.25
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 2.5 | 368 | 920
| TOTAL |  |  |  | 8587.7205
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1288.16
| TOTAL |  |  |  | 9875.8805
| Rate per meter |  |  |  | 197.5176
| Say |  |  |  | 198
198
Analysis of rate
1.20 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
1.20.4 | 40 mm |  | DSR | Rate Rs. | 293
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
1204 | 40 mm dia. ISI marked, steel conduit = 50.0 + 2.50 (Wastage @ 5%) = 52.50m | metre | 52.5 | 184.28 | 9674.7
1209 | 40 mm inspection/ solid bends | each | 4 | 34.13 | 136.52
1214 | 40 mm sockets | each | 15 | 13.86 | 207.9
1221 | 40 mm iron staples/ saddles/ screws | each | 85 | 4.31 | 366.35
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | LS | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 10413.77
| Cartage @ 1 % of A1 |  |  |  | 104.1377
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 12731.1977
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1909.68
| TOTAL |  |  |  | 14640.8777
| Rate per meter |  |  |  | 292.8176
| Say |  |  |  | 293
293
Analysis of rate
1.20 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
1.20.5 | 50 mm |  | DSR | Rate Rs. | 389
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
1205 | 50 mm dia. ISI marked, steel conduit = 50.0 + 2.50 (Wastage @ 5%) = 52.50m | metre | 52.5 | 259.88 | 13643.7
1210 | 50 mm inspection/ solid bends | each | 4 | 49.88 | 199.52
1215 | 50 mm sockets | each | 15 | 13.86 | 207.9
1222 | 50 mm iron staples/ saddles/ screws | each | 85 | 5.71 | 485.35
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | LS | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 14564.77
| Cartage @ 1 % of A1 |  |  |  | 145.6477
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 16923.7077
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2538.56
| TOTAL |  |  |  | 19462.2677
| Rate per meter |  |  |  | 389.2454
| Say |  |  |  | 389
389
Analysis of rate
1.21 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
1.21.1 | 20 mm |  | DSR | Rate Rs. | 57
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
1224 | 20 mm dia. ISI marked, PVC conduit = 50.0 + 2.50 (Wastage @ 5%) = 52.50m | metre | 52.5 | 11.81 | 620.03
1229 | 20 mm PVC bends | each | 4 | 5.65 | 22.6
1234 | 20 mm PVC couplers | each | 15 | 3.5 | 52.5
1218 | 20 mm iron staples/ saddles/ screws | each | 85 | 1.6 | 136
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | LS | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 859.43
| Cartage @ 1 % of A1 |  |  |  | 8.5943
LABOUR
1001 | Wireman | day | 1.25 | 447 | 558.75
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 2468.0243
| OVERHEADS & PROFIT @ 15 % |  |  |  | 370.2
| TOTAL |  |  |  | 2838.2243
| Rate per meter |  |  |  | 56.7645
| Say |  |  |  | 57
57
Analysis of rate
1.21 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
1.21.2 | 25 mm |  | DSR | Rate Rs. | 69
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
1225 | 25 mm dia. ISI marked, PVC conduit = 50.0 + 2.50 (Wastage @ 5%) = 52.50m | metre | 52.5 | 20.32 | 1066.8
1230 | 25 mm PVC bends | each | 4 | 7.7 | 30.8
1235 | 25 mm PVC couplers | each | 15 | 5.24 | 78.6
1219 | 25 mm iron staples/ saddles/ screws | each | 85 | 2.19 | 186.15
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | LS | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 1390.65
| Cartage @ 1 % of A1 |  |  |  | 13.9065
LABOUR
1001 | Wireman | day | 1.25 | 447 | 558.75
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 3004.5565
| OVERHEADS & PROFIT @ 15 % |  |  |  | 450.68
| TOTAL |  |  |  | 3455.2365
| Rate per meter |  |  |  | 69.1047
| Say |  |  |  | 69
69
Analysis of rate
1.21 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
1.21.3 | 32 mm |  | DSR | Rate Rs. | 89
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
1226 | 32 mm dia. ISI marked, PVC conduit = 50.0 + 2.50 (Wastage @ 5%) = 52.50m | metre | 52.5 | 33.59 | 1763.48
1231 | 32 mm PVC bends | each | 4 | 13.16 | 52.64
1236 | 32 mm PVC couplers | each | 15 | 8.55 | 128.25
1220 | 32 mm iron staples/ saddles/ screws | each | 85 | 3.34 | 283.9
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | LS | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 2256.57
| Cartage @ 1 % of A1 |  |  |  | 22.5657
LABOUR
1001 | Wireman | day | 1.25 | 447 | 558.75
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 3879.1357
| OVERHEADS & PROFIT @ 15 % |  |  |  | 581.87
| TOTAL |  |  |  | 4461.0057
| Rate per meter |  |  |  | 89.2201
| Say |  |  |  | 89
89
Analysis of rate
1.21 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
1.21.4 | 40 mm |  | DSR | Rate Rs. | 114
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
1227 | 40 mm dia. ISI marked, PVC conduit = 50.0 + 2.50 (Wastage @ 5%) = 52.50m | metre | 52.5 | 47.37 | 2486.93
1232 | 40 mm PVC bends | each | 4 | 20.98 | 83.92
1237 | 40 mm PVC couplers | each | 15 | 10.44 | 156.6
1221 | 40 mm iron staples/ saddles/ screws | each | 85 | 4.31 | 366.35
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | LS | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 3122.1
| Cartage @ 1 % of A1 |  |  |  | 31.221
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.25 | 368 | 828
| TOTAL |  |  |  | 4957.071
| OVERHEADS & PROFIT @ 15 % |  |  |  | 743.56
| TOTAL |  |  |  | 5700.631
| Rate per meter |  |  |  | 114.0126
| Say |  |  |  | 114
114
Analysis of rate
1.21 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
1.21.5 | 50 mm |  | DSR | Rate Rs. | 148
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
1228 | 50 mm dia. ISI marked, PVC conduit = 50.0 + 2.50 (Wastage @ 5%) = 52.50m | metre | 52.5 | 71.35 | 3745.88
1233 | 50 mm PVC bends | each | 4 | 34.07 | 136.28
1238 | 50 mm PVC couplers | each | 15 | 13.06 | 195.9
1222 | 50 mm iron staples/ saddles/ screws | each | 85 | 5.71 | 485.35
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
2935 | Cement, paint, sand etc. | LS | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 4591.71
| Cartage @ 1 % of A1 |  |  |  | 45.9171
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.25 | 368 | 828
| TOTAL |  |  |  | 6441.3771
| OVERHEADS & PROFIT @ 15 % |  |  |  | 966.21
| TOTAL |  |  |  | 7407.5871
| Rate per meter |  |  |  | 148.1517
| Say |  |  |  | 148
148
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.1 | 75 mm X 75 mm X 60 mm deep |  | DSR | Rate Rs. | 95
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1306 | 75 mm X 75 mm X 60 mm deep metal box | each | 1 | 20 | 20
1322 | 3 mm thick phenolic laminated sheet | sqcm | 64 | 0.1 | 6.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 2 | 0.4 | 0.8
2920 | Washers | each | 2 | 0.17 | 0.34
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 32.6
| Cartage @ 1 % of A1 |  |  |  | 0.326
LABOUR
1001 | Wireman | day | 0.02 | 447 | 8.94
1010 | Mason, Grade 2 | day | 0.04 | 407 | 16.28
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 82.266
| OVERHEADS & PROFIT @ 15 % |  |  |  | 12.34
| TOTAL |  |  |  | 94.606
| Rate per Each |  |  |  | 94.606
| Say |  |  |  | 95
95
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.2 | 100 mm X 100 mm X 60 mm deep |  | DSR | Rate Rs. | 114
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1307 | 100 mm X 100 mm X 60 mm deep metal box | each | 1 | 30.71 | 30.71
1322 | 3 mm thick phenolic laminated sheet | sqcm | 121 | 0.1 | 12.1
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 2 | 0.4 | 0.8
2920 | Washers | each | 2 | 0.17 | 0.34
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 49.01
| Cartage @ 1 % of A1 |  |  |  | 0.4901
LABOUR
1001 | Wireman | day | 0.02 | 447 | 8.94
1010 | Mason, Grade 2 | day | 0.04 | 407 | 16.28
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 98.8401
| OVERHEADS & PROFIT @ 15 % |  |  |  | 14.83
| TOTAL |  |  |  | 113.6701
| Rate per Each |  |  |  | 113.6701
| Say |  |  |  | 114
114
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.3 | 150 mm X 75 mm X 60 mm deep |  | DSR | Rate Rs. | 118
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1308 | 150 mm X 75 mm X 60 mm deep metal box | each | 1 | 32.55 | 32.55
1322 | 3 mm thick phenolic laminated sheet | sqcm | 136 | 0.1 | 13.6
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 2 | 0.4 | 0.8
2920 | Washers | each | 2 | 0.17 | 0.34
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 52.35
| Cartage @ 1 % of A1 |  |  |  | 0.5235
LABOUR
1001 | Wireman | day | 0.02 | 447 | 8.94
1010 | Mason, Grade 2 | day | 0.04 | 407 | 16.28
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 102.2135
| OVERHEADS & PROFIT @ 15 % |  |  |  | 15.33
| TOTAL |  |  |  | 117.5435
| Rate per Each |  |  |  | 117.5435
| Say |  |  |  | 118
118
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.4 | 150 mm X 150 mm X 60 mm deep |  | DSR | Rate Rs. | 168
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1309 | 150 mm X 150 mm X 60 mm deep metal box | each | 1 | 46.68 | 46.68
1322 | 3 mm thick phenolic laminated sheet | sqcm | 256 | 0.1 | 25.6
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 80.18
| Cartage @ 1 % of A1 |  |  |  | 0.8018
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 146.2218
| OVERHEADS & PROFIT @ 15 % |  |  |  | 21.93
| TOTAL |  |  |  | 168.1518
| Rate per Each |  |  |  | 168.1518
| Say |  |  |  | 168
168
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.5 | 180 mm X 100 mm X 60 mm |  | DSR | Rate Rs. | 133
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1310 | 180 mm X 100 mm X 60 mm deep metal box | each | 1 | 39.31 | 39.31
1322 | 3 mm thick phenolic laminated sheet | sqcm | 205 | 0.1 | 20.5
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 2 | 0.4 | 0.8
2920 | Washers | each | 2 | 0.17 | 0.34
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 66.01
| Cartage @ 1 % of A1 |  |  |  | 0.6601
LABOUR
1001 | Wireman | day | 0.02 | 447 | 8.94
1010 | Mason, Grade 2 | day | 0.04 | 407 | 16.28
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 116.0101
| OVERHEADS & PROFIT @ 15 % |  |  |  | 17.4
| TOTAL |  |  |  | 133.4101
| Rate per Each |  |  |  | 133.4101
| Say |  |  |  | 133
133
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.6 | 200 mm X 125 mm X 60 mm |  | DSR | Rate Rs. | 174
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1311 | 200 mm X 125 mm X 60 mm deep metal box | each | 1 | 49 | 49
1322 | 3 mm thick phenolic laminated sheet | sqcm | 284 | 0.1 | 28.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 85.3
| Cartage @ 1 % of A1 |  |  |  | 0.853
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 151.393
| OVERHEADS & PROFIT @ 15 % |  |  |  | 22.71
| TOTAL |  |  |  | 174.103
| Rate per Each |  |  |  | 174.103
| Say |  |  |  | 174
174
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.7 | 200 mm X 150 mm X 60 mm |  | DSR | Rate Rs. | 194
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1312 | 200 mm X 150 mm X 60 mm deep metal box | each | 1 | 61 | 61
1322 | 3 mm thick phenolic laminated sheet | sqcm | 336 | 0.1 | 33.6
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 102.5
| Cartage @ 1 % of A1 |  |  |  | 1.025
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 168.765
| OVERHEADS & PROFIT @ 15 % |  |  |  | 25.31
| TOTAL |  |  |  | 194.075
| Rate per Each |  |  |  | 194.075
| Say |  |  |  | 194
194
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.8 | 200 mm X 150 mm X 75 mm |  | DSR | Rate Rs. | 201
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1316 | 200 mm X 150 mm X 75 mm deep metal box | each | 1 | 67 | 67
1322 | 3 mm thick phenolic laminated sheet | sqcm | 336 | 0.1 | 33.6
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 108.5
| Cartage @ 1 % of A1 |  |  |  | 1.085
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 174.825
| OVERHEADS & PROFIT @ 15 % |  |  |  | 26.22
| TOTAL |  |  |  | 201.045
| Rate per Each |  |  |  | 201.045
| Say |  |  |  | 201
201
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.9 | 200 mm X 250 mm X 60 mm |  | DSR | Rate Rs. | 255
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1313 | 200 mm X 250 mm X 60 mm deep metal box | each | 1 | 79 | 79
1322 | 3 mm thick phenolic laminated sheet | sqcm | 557 | 0.1 | 55.7
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 2 | 4.5 | 9
| Total cost of materials |  |  |  | 147.1
| Cartage @ 1 % of A1 |  |  |  | 1.471
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.09 | 368 | 33.12
| TOTAL |  |  |  | 221.561
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.23
| TOTAL |  |  |  | 254.791
| Rate per Each |  |  |  | 254.791
| Say |  |  |  | 255
255
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.10 | 200 mm X 250 mm X 75 mm |  | DSR | Rate Rs. | 1234
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1317 | 200 mm X 250 mm X 75 mm deep metal box | each | 1 | 922 | 922
1322 | 3 mm thick phenolic laminated sheet | sqcm | 557 | 0.1 | 55.7
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 2 | 4.5 | 9
| Total cost of materials |  |  |  | 990.1
| Cartage @ 1 % of A1 |  |  |  | 9.901
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.09 | 368 | 33.12
| TOTAL |  |  |  | 1072.991
| OVERHEADS & PROFIT @ 15 % |  |  |  | 160.95
| TOTAL |  |  |  | 1233.941
| Rate per Each |  |  |  | 1233.941
| Say |  |  |  | 1234
1234
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.11 | 200 mm X 150 mm X 100 mm |  | DSR | Rate Rs. | 231
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1318 | 200 mm X 150 mm X 100 mm deep metal box | each | 1 | 81 | 81
1322 | 3 mm thick phenolic laminated sheet | sqcm | 336 | 0.1 | 33.6
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 2 | 4.5 | 9
| Total cost of materials |  |  |  | 127
| Cartage @ 1 % of A1 |  |  |  | 1.27
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.09 | 368 | 33.12
| TOTAL |  |  |  | 201.26
| OVERHEADS & PROFIT @ 15 % |  |  |  | 30.19
| TOTAL |  |  |  | 231.45
| Rate per Each |  |  |  | 231.45
| Say |  |  |  | 231
231
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.12 | 200 mm X 250 mm X 100 mm |  | DSR | Rate Rs. | 284
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1319 | 200 mm X 250 mm X 100 mm deep metal box | each | 1 | 104 | 104
1322 | 3 mm thick phenolic laminated sheet | sqcm | 557 | 0.1 | 55.7
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 2 | 4.5 | 9
| Total cost of materials |  |  |  | 172.1
| Cartage @ 1 % of A1 |  |  |  | 1.721
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.09 | 368 | 33.12
| TOTAL |  |  |  | 246.811
| OVERHEADS & PROFIT @ 15 % |  |  |  | 37.02
| TOTAL |  |  |  | 283.831
| Rate per Each |  |  |  | 283.831
| Say |  |  |  | 284
284
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.13 | 200 mm X 300 mm X 60 mm |  | DSR | Rate Rs. | 303
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1314 | 200 mm X 300 mm X 60 mm deep metal box | each | 1 | 110 | 110
1322 | 3 mm thick phenolic laminated sheet | sqcm | 662 | 0.1 | 66.2
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 2 | 4.5 | 9
| Total cost of materials |  |  |  | 188.6
| Cartage @ 1 % of A1 |  |  |  | 1.886
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.09 | 368 | 33.12
| TOTAL |  |  |  | 263.476
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.52
| TOTAL |  |  |  | 302.996
| Rate per Each |  |  |  | 302.996
| Say |  |  |  | 303
303
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.14 | 200 mm X 300 mm X 100 mm |  | DSR | Rate Rs. | 317
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1320 | 200 mm X 300 mm X 100 mm deep metal box | each | 1 | 122 | 122
1322 | 3 mm thick phenolic laminated sheet | sqcm | 662 | 0.1 | 66.2
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 2 | 4.5 | 9
| Total cost of materials |  |  |  | 200.6
| Cartage @ 1 % of A1 |  |  |  | 2.006
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.09 | 368 | 33.12
| TOTAL |  |  |  | 275.596
| OVERHEADS & PROFIT @ 15 % |  |  |  | 41.34
| TOTAL |  |  |  | 316.936
| Rate per Each |  |  |  | 316.936
| Say |  |  |  | 317
317
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.15 | 250 mm X 300 mm X 60 mm |  | DSR | Rate Rs. | 337
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1315 | 250 mm X 300 mm X 60 mm deep metal box | each | 1 | 122 | 122
1322 | 3 mm thick phenolic laminated sheet | sqcm | 835 | 0.1 | 83.5
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 2 | 4.5 | 9
| Total cost of materials |  |  |  | 217.9
| Cartage @ 1 % of A1 |  |  |  | 2.179
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.09 | 368 | 33.12
| TOTAL |  |  |  | 293.069
| OVERHEADS & PROFIT @ 15 % |  |  |  | 43.96
| TOTAL |  |  |  | 337.029
| Rate per Each |  |  |  | 337.029
| Say |  |  |  | 337
337
Analysis of rate
1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
1.22.16 | 250 mm X 300 mm X 100 mm |  | DSR | Rate Rs. | 373
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1321 | 250 mm X 300 mm X 100 mm deep metal box | each | 1 | 153 | 153
1322 | 3 mm thick phenolic laminated sheet | sqcm | 835 | 0.1 | 83.5
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 2 | 4.5 | 9
| Total cost of materials |  |  |  | 248.9
| Cartage @ 1 % of A1 |  |  |  | 2.489
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.09 | 368 | 33.12
| TOTAL |  |  |  | 324.379
| OVERHEADS & PROFIT @ 15 % |  |  |  | 48.66
| TOTAL |  |  |  | 373.039
| Rate per Each |  |  |  | 373.039
| Say |  |  |  | 373
373
Analysis of rate
1.23 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required.
1.23.1 | 5/6 amps switch |  | DSR | Rate Rs. | 34
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1431 | S.P. 5/6 amps, one way switch, piano type ISI marked | each | 1 | 13.3 | 13.3
| Total cost of materials |  |  |  | 13.3
| Cartage @ 1 % of A1 |  |  |  | 0.133
LABOUR
1001 | Wireman | day | 0.02 | 447 | 8.94
1007 | Khallasi | day | 0.02 | 368 | 7.36
| TOTAL |  |  |  | 29.733
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4.46
| TOTAL |  |  |  | 34.193
| Rate per Each |  |  |  | 34.193
| Say |  |  |  | 34
34
Analysis of rate
1.23 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required.
1.23.2 | 2 way 5/6 amps switch |  | DSR | Rate Rs. | 39
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1432 | S.P. 5/6 amps, two way switch, piano type ISI marked | each | 1 | 17.37 | 17.37
| Total cost of materials |  |  |  | 17.37
| Cartage @ 1 % of A1 |  |  |  | 0.1737
LABOUR
1001 | Wireman | day | 0.02 | 447 | 8.94
1007 | Khallasi | day | 0.02 | 368 | 7.36
| TOTAL |  |  |  | 33.8437
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5.08
| TOTAL |  |  |  | 38.9237
| Rate per Each |  |  |  | 38.9237
| Say |  |  |  | 39
39
Analysis of rate
1.23 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required.
1.23.3 | 15/16 amp switch |  | DSR | Rate Rs. | 75
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1433 | S.P. 15/16 amps, one way switch, piano type ISI marked | each | 1 | 40 | 40
| Total cost of materials |  |  |  | 40
| Cartage @ 1 % of A1 |  |  |  | 0.4
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 64.85
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9.73
| TOTAL |  |  |  | 74.58
| Rate per Each |  |  |  | 74.58
| Say |  |  |  | 75
75
Analysis of rate
1.23 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required.
1.23.4 | 3 pin 5/6 amp socket outlet |  | DSR | Rate Rs. | 42
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1434 | 3 pin 5/6 amps socket outlet, piano type ISI marked | each | 1 | 20.26 | 20.26
| Total cost of materials |  |  |  | 20.26
| Cartage @ 1 % of A1 |  |  |  | 0.2026
LABOUR
1001 | Wireman | day | 0.02 | 447 | 8.94
1007 | Khallasi | day | 0.02 | 368 | 7.36
| TOTAL |  |  |  | 36.7626
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5.51
| TOTAL |  |  |  | 42.2726
| Rate per Each |  |  |  | 42.2726
| Say |  |  |  | 42
42
Analysis of rate
1.23 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required.
1.23.5 | 6 pin 15/16 amp socket outlet |  | DSR | Rate Rs. | 86
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1435 | 6 pin 15/16 & 5/6 amps socket outlet, piano type ISI marked | each | 1 | 50 | 50
| Total cost of materials |  |  |  | 50
| Cartage @ 1 % of A1 |  |  |  | 0.5
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 74.95
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11.24
| TOTAL |  |  |  | 86.19
| Rate per Each |  |  |  | 86.19
| Say |  |  |  | 86
86
Analysis of rate
1.23 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required.
1.23.6 | Telephone socket outlet |  | DSR | Rate Rs. | 55
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1437 | Telephone Socket outlet piano type | each | 1 | 23.15 | 23.15
| Total cost of materials |  |  |  | 23.15
| Cartage @ 1 % of A1 |  |  |  | 0.2315
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 47.8315
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7.17
| TOTAL |  |  |  | 55.0015
| Rate per Each |  |  |  | 55.0015
| Say |  |  |  | 55
55
Analysis of rate
1.23 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required.
1.23.7 | TV antenna socket outlet |  | DSR | Rate Rs. | 48
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1438 | T.V. Socket outlet piano type | each | 1 | 17.37 | 17.37
| Total cost of materials |  |  |  | 17.37
| Cartage @ 1 % of A1 |  |  |  | 0.1737
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 41.9937
| OVERHEADS & PROFIT @ 15 % |  |  |  | 6.3
| TOTAL |  |  |  | 48.2937
| Rate per Each |  |  |  | 48.2937
| Say |  |  |  | 48
48
Analysis of rate
1.23 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required.
1.23.8 | Bell push |  | DSR | Rate Rs. | 47
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1436 | Bell push, piano type | each | 1 | 15.91 | 15.91
| Total cost of materials |  |  |  | 15.91
| Cartage @ 1 % of A1 |  |  |  | 0.1591
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 40.5191
| OVERHEADS & PROFIT @ 15 % |  |  |  | 6.08
| TOTAL |  |  |  | 46.5991
| Rate per Each |  |  |  | 46.5991
| Say |  |  |  | 47
47
Analysis of rate
1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
1.24.1 | 5/6 amps switch |  | DSR | Rate Rs. | 84
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1402 | S.P. 5/6 amps, one way modular switch, ISI marked | each | 1 | 48 | 48
| Total cost of materials |  |  |  | 48
| Cartage @ 1 % of A1 |  |  |  | 0.48
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 72.93
| OVERHEADS & PROFIT @ 15 % |  |  |  | 10.94
| TOTAL |  |  |  | 83.87
| Rate per Each |  |  |  | 83.87
| Say |  |  |  | 84
84
Analysis of rate
1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
1.24.2 | 2 way 5/6 amps switch |  | DSR | Rate Rs. | 99
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1403 | S.P. 5/6 amps, two way modular switch, ISI marked | each | 1 | 60.8 | 60.8
| Total cost of materials |  |  |  | 60.8
| Cartage @ 1 % of A1 |  |  |  | 0.608
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 85.858
| OVERHEADS & PROFIT @ 15 % |  |  |  | 12.88
| TOTAL |  |  |  | 98.738
| Rate per Each |  |  |  | 98.738
| Say |  |  |  | 99
99
Analysis of rate
1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
1.24.3 | 15/16 amp switch |  | DSR | Rate Rs. | 114
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1404 | S.P. 15/16 amps, one way modular switch, ISI marked | each | 1 | 73.6 | 73.6
| Total cost of materials |  |  |  | 73.6
| Cartage @ 1 % of A1 |  |  |  | 0.736
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 98.786
| OVERHEADS & PROFIT @ 15 % |  |  |  | 14.82
| TOTAL |  |  |  | 113.606
| Rate per Each |  |  |  | 113.606
| Say |  |  |  | 114
114
Analysis of rate
1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
1.24.4 | 3 pin 5/6 amp socket outlet |  | DSR | Rate Rs. | 81
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1405 | 3 pin 5/6 amps modular socket outlet, ISI marked | each | 1 | 53.6 | 53.6
| Total cost of materials |  |  |  | 53.6
| Cartage @ 1 % of A1 |  |  |  | 0.536
LABOUR
1001 | Wireman | day | 0.02 | 447 | 8.94
1007 | Khallasi | day | 0.02 | 368 | 7.36
| TOTAL |  |  |  | 70.436
| OVERHEADS & PROFIT @ 15 % |  |  |  | 10.57
| TOTAL |  |  |  | 81.006
| Rate per Each |  |  |  | 81.006
| Say |  |  |  | 81
81
Analysis of rate
1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
1.24.5 | 6 pin 15/16 amp socket outlet |  | DSR | Rate Rs. | 153
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1406 | 6 pin 15/16 amps modular socket outlet, ISI marked | each | 1 | 107.6 | 107.6
| Total cost of materials |  |  |  | 107.6
| Cartage @ 1 % of A1 |  |  |  | 1.076
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 133.126
| OVERHEADS & PROFIT @ 15 % |  |  |  | 19.97
| TOTAL |  |  |  | 153.096
| Rate per Each |  |  |  | 153.096
| Say |  |  |  | 153
153
Analysis of rate
1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
1.24.6 | Telephone socket outlet |  | DSR | Rate Rs. | 96
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1409 | Telephone Socket outlet modular type | each | 1 | 58.5 | 58.5
| Total cost of materials |  |  |  | 58.5
| Cartage @ 1 % of A1 |  |  |  | 0.585
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 83.535
| OVERHEADS & PROFIT @ 15 % |  |  |  | 12.53
| TOTAL |  |  |  | 96.065
| Rate per Each |  |  |  | 96.065
| Say |  |  |  | 96
96
Analysis of rate
1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
1.23.7 | TV antenna socket outlet |  | DSR | Rate Rs. | 97
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1410 | T.V. Socket outlet modular type | each | 1 | 59.2 | 59.2
| Total cost of materials |  |  |  | 59.2
| Cartage @ 1 % of A1 |  |  |  | 0.592
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 84.242
| OVERHEADS & PROFIT @ 15 % |  |  |  | 12.64
| TOTAL |  |  |  | 96.882
| Rate per Each |  |  |  | 96.882
| Say |  |  |  | 97
97
Analysis of rate
1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
1.24.8 | Bell push |  | DSR | Rate Rs. | 114
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1407 | Modular bell push, ISI marked | each | 1 | 73.6 | 73.6
| Total cost of materials |  |  |  | 73.6
| Cartage @ 1 % of A1 |  |  |  | 0.736
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 98.786
| OVERHEADS & PROFIT @ 15 % |  |  |  | 14.82
| TOTAL |  |  |  | 113.606
| Rate per Each |  |  |  | 113.606
| Say |  |  |  | 114
114
Analysis of rate
1.25 | Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required.
|  |  | DSR | Rate Rs. | 288
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1408 | Stepped type Modular Fan regulator (2 module) | each | 1 | 216 | 216
| Total cost of materials |  |  |  | 216
| Cartage @ 1 % of A1 |  |  |  | 2.16
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 250.76
| OVERHEADS & PROFIT @ 15 % |  |  |  | 37.61
| TOTAL |  |  |  | 288.37
| Rate per Each |  |  |  | 288.37
| Say |  |  |  | 288
288
Analysis of rate
1.26 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required.
|  |  | DSR | Rate Rs. | 24
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1411 | Modular blanking plate | each | 1 | 12.8 | 12.8
| Total cost of materials |  |  |  | 12.8
| Cartage @ 1 % of A1 |  |  |  | 0.128
LABOUR
1001 | Wireman | day | 0.01 | 447 | 4.47
1007 | Khallasi | day | 0.01 | 368 | 3.68
| TOTAL |  |  |  | 21.078
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3.16
| TOTAL |  |  |  | 24.238
| Rate per Each |  |  |  | 24.238
| Say |  |  |  | 24
24
Analysis of rate
1.27 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
1.27.1 | 1 or 2 Module (75mmX75mm) |  | DSR | Rate Rs. | 175
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1300 | Modular GI box for 2 module | each | 1 | 28 | 28
1421 | Modular base & cover plate for 2 module | each | 1 | 39.6 | 39.6
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 72.66
| Cartage @ 1 % of A1 |  |  |  | 0.7266
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 152.4866
| OVERHEADS & PROFIT @ 15 % |  |  |  | 22.87
| TOTAL |  |  |  | 175.3566
| Rate per Each |  |  |  | 175.3566
| Say |  |  |  | 175
175
Analysis of rate
1.27 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
1.27.2 | 3 Module (100mmX75mm) |  | DSR | Rate Rs. | 185
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1301 | Modular GI box for 3 module | each | 1 | 29.6 | 29.6
1422 | Modular base & cover plate for 3 module | each | 1 | 46.4 | 46.4
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 81.06
| Cartage @ 1 % of A1 |  |  |  | 0.8106
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 160.9706
| OVERHEADS & PROFIT @ 15 % |  |  |  | 24.15
| TOTAL |  |  |  | 185.1206
| Rate per Each |  |  |  | 185.1206
| Say |  |  |  | 185
185
Analysis of rate
1.27 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
1.27.3 | 4 Module (125mmX75mm) |  | DSR | Rate Rs. | 205
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1302 | Modular GI box for 4 module | each | 1 | 38.4 | 38.4
1423 | Modular base & cover plate for 4 module | each | 1 | 54.8 | 54.8
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 98.26
| Cartage @ 1 % of A1 |  |  |  | 0.9826
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 178.3426
| OVERHEADS & PROFIT @ 15 % |  |  |  | 26.75
| TOTAL |  |  |  | 205.0926
| Rate per Each |  |  |  | 205.0926
| Say |  |  |  | 205
205
Analysis of rate
1.27 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
1.27.4 | 6 Module (200mmX75mm) |  | DSR | Rate Rs. | 258
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1303 | Modular GI box for 6 module | each | 1 | 62 | 62
1424 | Modular base & cover plate for 6 module | each | 1 | 76.4 | 76.4
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 143.46
| Cartage @ 1 % of A1 |  |  |  | 1.4346
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 223.9946
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.6
| TOTAL |  |  |  | 257.5946
| Rate per Each |  |  |  | 257.5946
| Say |  |  |  | 258
258
Analysis of rate
1.27 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
1.27.5 | 8 Module (125mmX125mm) |  | DSR | Rate Rs. | 297
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1304 | Modular GI box for 8 module | each | 1 | 74 | 74
1425 | Modular base & cover plate for 8 module | each | 1 | 97.6 | 97.6
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 177.22
| Cartage @ 1 % of A1 |  |  |  | 1.7722
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 258.0922
| OVERHEADS & PROFIT @ 15 % |  |  |  | 38.71
| TOTAL |  |  |  | 296.8022
| Rate per Each |  |  |  | 296.8022
| Say |  |  |  | 297
297
Analysis of rate
1.27 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
1.27.6 | 12 Module (200mmX150mm) |  | DSR | Rate Rs. | 344
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1305 | Modular GI box for 12 module | each | 1 | 102 | 102
1426 | Modular base & cover plate for 12 module | each | 1 | 110.4 | 110.4
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 218.02
| Cartage @ 1 % of A1 |  |  |  | 2.1802
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1010 | Mason, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 299.3002
| OVERHEADS & PROFIT @ 15 % |  |  |  | 44.9
| TOTAL |  |  |  | 344.2002
| Rate per Each |  |  |  | 344.2002
| Say |  |  |  | 344
344
Analysis of rate
1.28 | Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.
1.28.1 | 1 or 2 Module |  | DSR | Rate Rs. | 83
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1420 | Modular base & cover plate for 1 module | each | 1 | 38.8 | 38.8
| Total cost of materials |  |  |  | 38.8
| Cartage @ 1 % of A1 |  |  |  | 0.388
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 71.788
| OVERHEADS & PROFIT @ 15 % |  |  |  | 10.77
| TOTAL |  |  |  | 82.558
| Rate per Each |  |  |  | 82.558
| Say |  |  |  | 83
83
Analysis of rate
1.28 | Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.
1.28.2 | 3 Module |  | DSR | Rate Rs. | 91
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1422 | Modular base & cover plate for 3 module | each | 1 | 46.4 | 46.4
| Total cost of materials |  |  |  | 46.4
| Cartage @ 1 % of A1 |  |  |  | 0.464
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 79.464
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11.92
| TOTAL |  |  |  | 91.384
| Rate per Each |  |  |  | 91.384
| Say |  |  |  | 91
91
Analysis of rate
1.28 | Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.
1.28.3 | 4 Module |  | DSR | Rate Rs. | 101
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1423 | Modular base & cover plate for 4 module | each | 1 | 54.8 | 54.8
| Total cost of materials |  |  |  | 54.8
| Cartage @ 1 % of A1 |  |  |  | 0.548
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 87.948
| OVERHEADS & PROFIT @ 15 % |  |  |  | 13.19
| TOTAL |  |  |  | 101.138
| Rate per Each |  |  |  | 101.138
| Say |  |  |  | 101
101
Analysis of rate
1.28 | Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.
1.28.4 | 6 Module |  | DSR | Rate Rs. | 126
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1424 | Modular base & cover plate for 6 module | each | 1 | 76.4 | 76.4
| Total cost of materials |  |  |  | 76.4
| Cartage @ 1 % of A1 |  |  |  | 0.764
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 109.764
| OVERHEADS & PROFIT @ 15 % |  |  |  | 16.46
| TOTAL |  |  |  | 126.224
| Rate per Each |  |  |  | 126.224
| Say |  |  |  | 126
126
Analysis of rate
1.28 | Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.
1.28.5 | 8 Module |  | DSR | Rate Rs. | 151
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1425 | Modular base & cover plate for 8 module | each | 1 | 97.6 | 97.6
| Total cost of materials |  |  |  | 97.6
| Cartage @ 1 % of A1 |  |  |  | 0.976
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 131.176
| OVERHEADS & PROFIT @ 15 % |  |  |  | 19.68
| TOTAL |  |  |  | 150.856
| Rate per Each |  |  |  | 150.856
| Say |  |  |  | 151
151
Analysis of rate
1.28 | Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.
1.28.6 | 12 Module |  | DSR | Rate Rs. | 166
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1426 | Modular base & cover plate for 12 module | each | 1 | 110.4 | 110.4
| Total cost of materials |  |  |  | 110.4
| Cartage @ 1 % of A1 |  |  |  | 1.104
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 144.104
| OVERHEADS & PROFIT @ 15 % |  |  |  | 21.62
| TOTAL |  |  |  | 165.724
| Rate per Each |  |  |  | 165.724
| Say |  |  |  | 166
166
Analysis of rate
1.29 | Supplying and fixing metal box of 150mm X 75mm X 60mm deep (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including providing and fixing 3 pin 5/6 amps socket outlet and 5/6 amps piano type switch, connection, painting etc. as required. (For light plugs to be used in non residential buildings).
|  |  | DSR | Rate Rs. | 205
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1308 | 150 mm X 75 mm X 60 mm deep metal box | each | 1 | 32.55 | 32.55
1322 | 3 mm thick phenolic laminated sheet | sqcm | 136 | 0.1 | 13.6
1434 | 3 pin 5/6 amps socket outlet, piano type ISI marked | each | 1 | 20.26 | 20.26
1431 | S.P. 5/6 amps, one way switch, piano type ISI marked | each | 1 | 13.3 | 13.3
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 87.05
| Cartage @ 1 % of A1 |  |  |  | 0.8705
LABOUR
1001 | Wireman | day | 0.07 | 447 | 31.29
1010 | Mason, Grade 2 | day | 0.04 | 407 | 16.28
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.11 | 368 | 40.48
| TOTAL |  |  |  | 178.0105
| OVERHEADS & PROFIT @ 15 % |  |  |  | 26.7
| TOTAL |  |  |  | 204.7105
| Rate per Each |  |  |  | 204.7105
| Say |  |  |  | 205
205
Analysis of rate
1.30 | Supplying and fixing metal box of 180mm X 100mm X 60mm deep (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including providing and fixing 6 pin 5/6 & 15/16 amps socket outlet and 15/16 amps piano type switch, connection, painting etc. as required.
|  |  | DSR | Rate Rs. | 287
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1310 | 180 mm X 100 mm X 60 mm deep metal box | each | 1 | 39.31 | 39.31
1322 | 3 mm thick phenolic laminated sheet | sqcm | 209 | 0.1 | 20.9
1435 | 6 pin 15/16 & 5/6 amps socket outlet, piano type ISI marked | each | 1 | 50 | 50
1433 | S.P. 15/16 amps, one way switch, piano type ISI marked | each | 1 | 40 | 40
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 4 | 0.4 | 1.6
2920 | Washers | each | 4 | 0.17 | 0.68
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 157.55
| Cartage @ 1 % of A1 |  |  |  | 1.5755
LABOUR
1001 | Wireman | day | 0.07 | 447 | 31.29
1010 | Mason, Grade 2 | day | 0.04 | 407 | 16.28
1006 | Painter | day | 0.005 | 407 | 2.04
1007 | Khallasi | day | 0.11 | 368 | 40.48
| TOTAL |  |  |  | 249.2155
| OVERHEADS & PROFIT @ 15 % |  |  |  | 37.38
| TOTAL |  |  |  | 286.5955
| Rate per Each |  |  |  | 286.5955
| Say |  |  |  | 287
287
Analysis of rate
1.31 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings).
|  |  | DSR | Rate Rs. | 313
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1301 | Modular GI box for 3 module | each | 1 | 29.6 | 29.6
1405 | 3 pin 5/6 amps modular socket outlet, ISI marked | each | 1 | 53.6 | 53.6
1402 | S.P. 5/6 amps, one way modular switch, ISI marked | each | 1 | 48 | 48
1422 | Modular base & cover plate for 3 module | each | 1 | 46.4 | 46.4
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 182.66
| Cartage @ 1 % of A1 |  |  |  | 1.8266
LABOUR
1001 | Wireman | day | 0.07 | 447 | 31.29
1010 | Mason, Grade 2 | day | 0.04 | 407 | 16.28
1007 | Khallasi | day | 0.11 | 368 | 40.48
| TOTAL |  |  |  | 272.5366
| OVERHEADS & PROFIT @ 15 % |  |  |  | 40.88
| TOTAL |  |  |  | 313.4166
| Rate per Each |  |  |  | 313.4166
| Say |  |  |  | 313
313
Analysis of rate
1.32 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required.
|  |  | DSR | Rate Rs. | 406
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1301 | Modular GI box for 3 module | each | 1 | 29.6 | 29.6
1406 | 6 pin 15/16 amps modular socket outlet, ISI marked | each | 1 | 107.6 | 107.6
1404 | S.P. 15/16 amps, one way modular switch, ISI marked | each | 1 | 73.6 | 73.6
1422 | Modular base & cover plate for 3 module | each | 1 | 46.4 | 46.4
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 262.26
| Cartage @ 1 % of A1 |  |  |  | 2.6226
LABOUR
1001 | Wireman | day | 0.07 | 447 | 31.29
1010 | Mason, Grade 2 | day | 0.04 | 407 | 16.28
1007 | Khallasi | day | 0.11 | 368 | 40.48
| TOTAL |  |  |  | 352.9326
| OVERHEADS & PROFIT @ 15 % |  |  |  | 52.94
| TOTAL |  |  |  | 405.8726
| Rate per Each |  |  |  | 405.8726
| Say |  |  |  | 406
406
Analysis of rate
1.33 | Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required.
|  |  | DSR | Rate Rs. | 46
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1401 | Ceiling rose, 3 pin, 5 amps ISI marked | each | 1 | 14.4 | 14.4
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 2 | 0.4 | 0.8
| Total cost of materials |  |  |  | 15.2
| Cartage @ 1 % of A1 |  |  |  | 0.152
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 39.802
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5.97
| TOTAL |  |  |  | 45.772
| Rate per Each |  |  |  | 45.772
| Say |  |  |  | 46
46
Analysis of rate
1.34 | Supplying and fixing brass batten/ angle holder including connection etc. as required.
|  |  | DSR | Rate Rs. | 75
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1442 | Brass batten/ angle holder | each | 1 | 31 | 31
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 3 | 0.4 | 1.2
| Total cost of materials |  |  |  | 32.2
| Cartage @ 1 % of A1 |  |  |  | 0.322
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 65.122
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9.77
| TOTAL |  |  |  | 74.892
| Rate per Each |  |  |  | 74.892
| Say |  |  |  | 75
75
Analysis of rate
1.35 | Erection of wall bracket /ceiling fittings of all sizes and shapes containing upto two GLS lamps per fitting, complete with all accessories including connection etc. as required.
|  |  | DSR | Rate Rs. | 58
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 3 | 0.4 | 1.2
| Total cost of materials |  |  |  | 1.2
| Cartage @ 1 % of A1 |  |  |  | 0.012
LABOUR
1001 | Wireman | day | 0.06 | 447 | 26.82
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 50.112
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7.52
| TOTAL |  |  |  | 57.632
| Rate per Each |  |  |  | 57.632
| Say |  |  |  | 58
58
Analysis of rate
1.36 | Supplying and fixing stiff pendent with 300 mm long, 20 mm dia X 1.6 mm thick steel conduit, aluminium cast back plate and brass holder complete, including wiring the down rod with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and painting etc. as required.
|  |  | DSR | Rate Rs. | 169
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1201 | 20 mm dia. ISI marked, steel conduit | metre | 0.32 | 60.01 | 19.2
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 0.79 | 11.1 | 8.77
= 0.75 + 0.04 (Wastage @5%) = 0.79m
2908 | Brass nipple | each | 1 | 6 | 6
2928 | Back plate | each | 1 | 6 | 6
1443 | Brass bracket holder 16 mm | each | 1 | 38 | 38
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 3 | 0.4 | 1.2
2944 | Paint | letre | 0.01 | 142 | 1.42
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
| Total cost of materials |  |  |  | 81.15
| Cartage @ 1 % of A1 |  |  |  | 0.8115
LABOUR
1001 | Wireman | day | 0.06 | 447 | 26.82
1010 | Mason, Grade 2 | day | 0.04 | 407 | 16.28
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 147.1415
| OVERHEADS & PROFIT @ 15 % |  |  |  | 22.07
| TOTAL |  |  |  | 169.2115
| Rate per Each |  |  |  | 169.2115
| Say |  |  |  | 169
169
Analysis of rate
1.37 | Supplying and fixing stiff pendent with 600 mm long, 20 mm dia X 1.6 mm thick steel conduit, aluminium cast back plate and brass holder complete, including wiring the down rod with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and painting etc. as required.
|  |  | DSR | Rate Rs. | 0
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1201 | 20 mm dia. ISI marked, steel conduit | metre | 0.63 | 60.01 | 37.81
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 1.42 | 11.1 | 15.76
= 0.75 + 0.04 (Wastage @5%) = 0.79m
2908 | Brass nipple | each | 1 | 6 | 6
2928 | Back plate | each | 1 | 6 | 6
1443 | Brass bracket holder 16 mm | each | 1 | 38 | 38
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 3 | 0.4 | 1.2
2944 | Paint | letre | 0.02 | 142 | 2.84
2857 | PVC fastener 40mm long | each | 2 | 0.28 | 0.56
| Total cost of materials |  |  |  | 108.17
| Cartage @ 1 % of A1 |  |  |  | 1.0817
LABOUR
1001 | Wireman | day | 0.06 | 447 | 26.82
1010 | Mason, Grade 2 | day | 0.04 | 407 | 16.28
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 174.4317
| OVERHEADS & PROFIT @ 15 % |  |  |  | 26.16
| TOTAL |  |  |  | 200.5917
| Rate per Each |  |  |  | 200.5917
| Say |  |  |  | 201
201
Analysis of rate
1.38 | Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required.
|  |  | DSR | Rate Rs. | 61
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1444 | Call bell/ buzzer, single phase | each | 1 | 35.38 | 35.38
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 2 | 0.4 | 0.8
| Total cost of materials |  |  |  | 36.18
| Cartage @ 1 % of A1 |  |  |  | 0.3618
LABOUR
1001 | Wireman | day | 0.02 | 447 | 8.94
1007 | Khallasi | day | 0.02 | 368 | 7.36
| TOTAL |  |  |  | 52.8418
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7.93
| TOTAL |  |  |  | 60.7718
| Rate per Each |  |  |  | 60.7718
| Say |  |  |  | 61
61
Analysis of rate
1.39 | Providing and fixing plain 16/0.20mm (0.50sqmm) twin flat flexible, FRLS PVC insulated, copper cable, in PVC sleeve of suitable size on the floor/ wall, or side of the table/ door etc. as required.
|  |  | DSR | Rate Rs. | 22
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1108 | 16/0.20 mm (0.5 sqmm) twin core FRLS PVC sheathed, flat flexible copper cable | metre | 53.03 | 11.52 | 610.91
| Total cost of materials |  |  |  | 610.91
| Cartage @ 1 % of A1 |  |  |  | 6.1091
LABOUR
1001 | Wireman | day | 0.4 | 447 | 178.8
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 943.0191
| OVERHEADS & PROFIT @ 15 % |  |  |  | 141.45
| TOTAL |  |  |  | 1084.4691
| Rate per meter |  |  |  | 21.6894
| Say |  |  |  | 22
22
Analysis of rate
1.40 | Providing and fixing plain 16/0.20mm (0.50sqmm) twin circular flexible FRLS PVC insulated, PVC sheathed copper cable direct on the wall with PVC clips etc. as required.
|  |  | DSR | Rate Rs. | 19
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1109 | 16/0.20 mm (0.5 sqmm) twin circular, FRLS PVC sheathed, workshop flexible copper cable | metre | 53.03 | 11.52 | 610.91
2858 | PVC clip for fixing cable | each | 100 | 0.1 | 10
| Total cost of materials |  |  |  | 620.91
| Cartage @ 1 % of A1 |  |  |  | 6.2091
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 830.8691
| OVERHEADS & PROFIT @ 15 % |  |  |  | 124.63
| TOTAL |  |  |  | 955.4991
| Rate per meter |  |  |  | 19.11
| Say |  |  |  | 19
19
Analysis of rate
1.41 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required.
|  |  | DSR | Rate Rs. | 100
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 0.32 | 11.1 | 3.55
= 0.30 + 0.02 (Wastage @5%) = 0.32m
2852 | Iron screws, 35 mm X 6 mm | each | 2 | 0.95 | 1.9
2857 | PVC fastener 40mm long | each | 1 | 0.28 | 0.28
| Total cost of materials |  |  |  | 5.73
| Cartage @ 1 % of A1 |  |  |  | 0.0573
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 87.2873
| OVERHEADS & PROFIT @ 15 % |  |  |  | 13.09
| TOTAL |  |  |  | 100.3773
| Rate per Each |  |  |  | 100.3773
| Say |  |  |  | 100
100
Analysis of rate
1.42 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required.
|  |  | DSR | Rate Rs. | 247
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 0.95 | 11.1 | 10.55
= 0.90 + 0.05 (Wastage @5%) = 0.95m
1201 | 20 mm dia. ISI marked, steel conduit | metre | 0.63 | 60.01 | 37.81
= 0.60 + 0.03 (Wastage @5%) = 0.63m
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 6 | 0.4 | 2.4
2927 | Ball and socket | each | 2 | 14 | 28
2929 | Check nut 20mm | each | 4 | 3 | 12
2859 | Rubber/ PVC bushes | each | 1 | 0.5 | 0.5
2944 | Paint | letre | 0.02 | 142 | 2.84
2857 | PVC fastener 40mm long | each | 6 | 0.28 | 1.68
| Total cost of materials |  |  |  | 95.78
| Cartage @ 1 % of A1 |  |  |  | 0.9578
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1006 | Painter | day | 0.03 | 407 | 12.21
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 214.8978
| OVERHEADS & PROFIT @ 15 % |  |  |  | 32.23
| TOTAL |  |  |  | 247.1278
| Rate per Each |  |  |  | 247.1278
| Say |  |  |  | 247
247
Analysis of rate
1.43 | Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored)
|  |  | DSR | Rate Rs. | 32
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1201 | 20 mm dia. ISI marked, steel conduit | metre | 0.2 | 60.01 | 12
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 0.2 | 11.1 | 2.22
2944 | Paint | letre | 0.01 | 142 | 1.42
| Total cost of materials |  |  |  | 15.64
| Cartage @ 1 % of A1 |  |  |  | 0.1564
LABOUR
1001 | Wireman | day | 0.01 | 447 | 4.47
1006 | Painter | day | 0.01 | 407 | 4.07
1007 | Khallasi | day | 0.01 | 368 | 3.68
| TOTAL |  |  |  | 28.0164
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4.2
| TOTAL |  |  |  | 32.2164
| Rate per Each |  |  |  | 32.2164
| Say |  |  |  | 32
32
Analysis of rate
1.44 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required.
|  |  | DSR | Rate Rs. | 105
COST FOR 10 NOS OF FANS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 8.4 | 11.1 | 93.24
= 8.0 + 0.40 (Wastage @5%) = 8.40m
| Total cost of materials |  |  |  | 93.24
| Cartage @ 1 % of A1 |  |  |  | 0.9324
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 909.1724
| OVERHEADS & PROFIT @ 15 % |  |  |  | 136.38
| TOTAL |  |  |  | 1045.5524
| Rate per Fan |  |  |  | 104.5552
| Say |  |  |  | 105
105
Analysis of rate
1.45 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable, including providing and fixing phenolic laminated sheet cover on the fan box etc. as required.
|  |  | DSR | Rate Rs. | 132
COST FOR 10 NOS OF FANS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 8.4 | 11.1 | 93.24
= 8.0 + 0.40 (Wastage @5%) = 8.40m
1322 | 3 mm thick phenolic laminated sheet | sqcm | 2312 | 0.1 | 231.2
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 16 | 0.4 | 6.4
2920 | Washers | each | 16 | 0.17 | 2.72
| Total cost of materials |  |  |  | 333.56
| Cartage @ 1 % of A1 |  |  |  | 3.3356
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 1151.8956
| OVERHEADS & PROFIT @ 15 % |  |  |  | 172.78
| TOTAL |  |  |  | 1324.6756
| Rate per Fan |  |  |  | 132.4676
| Say |  |  |  | 132
132
Analysis of rate
1.46 | Installation, testing and commissioning of resistance type ceiling fan regulator, in existing switch box including connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable, earthing the regulator etc. as required.
|  |  | DSR | Rate Rs. | 0
COST FOR 10 FANS REGULATOR
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1101 | 1.5 sq. mm ISI marked, FRLS PVC insulated, single core copper conductor cable | metre | 6.3 | 11.1 | 69.93
= 3x0.25x8 = 6.0 + 0.30 (Wastage @ 5%) = 6.30m
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 32 | 0.4 | 12.8
| Total cost of materials |  |  |  | 82.73
| Cartage @ 1 % of A1 |  |  |  | 0.8273
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 491.0573
| OVERHEADS & PROFIT @ 15 % |  |  |  | 73.66
| TOTAL |  |  |  | 564.7173
| Rate per Fan |  |  |  | 56.4717
| Say |  |  |  | 56
56
Analysis of rate
1.47 | Supplying and fixing extra down rod of 10 cm length G.I. pipe ,15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored)
|  |  | DSR | Rate Rs. | 22
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2827 | 15 mm dia. G.I. pipe (heavy class) | metre | 0.105 | 87.46 | 9.18
= 0.10 + 0.005 (Wastage @ 5%) = 0.105m
2944 | Paint | letre | 0.01 | 142 | 1.42
| Total cost of materials |  |  |  | 10.6
| Cartage @ 1 % of A1 |  |  |  | 0.106
LABOUR
1001 | Wireman | day | 0.007 | 447 | 3.13
1006 | Painter | day | 0.007 | 407 | 2.85
1007 | Khallasi | day | 0.007 | 368 | 2.58
| TOTAL |  |  |  | 19.266
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2.89
| TOTAL |  |  |  | 22.156
| Rate per Each |  |  |  | 22.156
| Say |  |  |  | 22
22
Analysis of rate
1.48 | Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored)
|  |  | DSR | Rate Rs. | 25
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2828 | 20 mm dia. G.I. pipe (heavy class) | metre | 0.105 | 112.75 | 11.84
= 0.10 + 0.005 (Wastage @ 5%) = 0.105m
2944 | Paint | letre | 0.01 | 142 | 1.42
| Total cost of materials |  |  |  | 13.26
| Cartage @ 1 % of A1 |  |  |  | 0.1326
LABOUR
1001 | Wireman | day | 0.007 | 447 | 3.13
1006 | Painter | day | 0.007 | 407 | 2.85
1007 | Khallasi | day | 0.007 | 368 | 2.58
| TOTAL |  |  |  | 21.9526
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3.29
| TOTAL |  |  |  | 25.2426
| Rate per Each |  |  |  | 25.2426
| Say |  |  |  | 25
25
Analysis of rate
1.49 | Numbering of ceiling fan/ exhaust fan/ fluorescent fittings as required.
|  |  | DSR | Rate Rs. | 28
COST FOR 100 FANS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2944 | Paint | letre | 1 | 142 | 142
| Total cost of materials |  |  |  | 142
| Cartage @ 1 % of A1 |  |  |  | 1.42
LABOUR
1006 | Painter | day | 3 | 407 | 1221
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 2468.42
| OVERHEADS & PROFIT @ 15 % |  |  |  | 370.26
| Cost for 100 Fans |  |  |  | 2838.68
| Rate per Each |  |  |  | 28.3868
| Say |  |  |  | 28
28
Analysis of rate
1.50 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
1.50.1 | Upto 450 mm sweep |  | DSR | Rate Rs. | 224
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
1108 | 16/0.20 mm (0.5 sqmm) twin core FRLS PVC sheathed, flat flexible copper cable | metre | 1 | 11.52 | 11.52
| Total cost of materials |  |  |  | 31.52
| Cartage @ 1 % of A1 |  |  |  | 0.3152
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 194.8352
| OVERHEADS & PROFIT @ 15 % |  |  |  | 29.23
| TOTAL |  |  |  | 224.0652
| Rate per Each |  |  |  | 224.0652
| Say |  |  |  | 224
224
Analysis of rate
1.5 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
1.50.2 | 510 mm sweep |  | DSR | Rate Rs. | 318
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
1108 | 16/0.20 mm (0.5 sqmm) twin core FRLS PVC sheathed, flat flexible copper cable | metre | 1 | 11.52 | 11.52
| Total cost of materials |  |  |  | 31.52
| Cartage @ 1 % of A1 |  |  |  | 0.3152
LABOUR
1001 | Wireman | day | 0.3 | 447 | 134.1
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 276.3352
| OVERHEADS & PROFIT @ 15 % |  |  |  | 41.45
| TOTAL |  |  |  | 317.7852
| Rate per Each |  |  |  | 317.7852
| Say |  |  |  | 318
318
Analysis of rate
1.51 | Extra for fixing the louvers/ shutters complete with frame for a exhaust fan of all sizes.
|  |  | DSR | Rate Rs. | 99
COST FOR EACH
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2853 | Iron screws, 40 mm X 6 mm | each | 4 | 0.95 | 3.8
2857 | PVC fastener 40mm long | each | 4 | 0.28 | 1.12
| Total cost of materials |  |  |  | 4.92
| Cartage @ 1 % of A1 |  |  |  | 0.0492
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 86.4692
| OVERHEADS & PROFIT @ 15 % |  |  |  | 12.97
| TOTAL |  |  |  | 99.4392
| Rate per Each |  |  |  | 99.4392
| Say |  |  |  | 99
99
Analysis of rate
1.52 | Painting of ceiling fan in installed position with one or more coats of spray painting with synthetic enamel paint of approved brand and manufacture to give an even shade, including cleaning of surface with detergent etc as required.
|  |  | DSR | Rate Rs. | 89
COST FOR 50 FANS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2944 | Paint | letre | 2.7 | 142 | 383.4
2939 | Cleaning materials like soap/ detergent | kg | 1 | 43 | 43
2938 | Cotton waste, cleaning cloth etc. | kg | 2 | 38 | 76
| Total cost of materials |  |  |  | 502.4
| Cartage @ 1 % of A1 |  |  |  | 5.024
LABOUR
1006 | Painter | day | 3 | 407 | 1221
1007 | Khallasi | day | 3 | 368 | 1104
1082 | Hire charges for compressor and spray gun | day | 3 | 350 | 1050
| TOTAL |  |  |  | 3882.424
| OVERHEADS & PROFIT @ 15 % |  |  |  | 582.36
| Cost for 100 Fans |  |  |  | 4464.784
| Rate per Each |  |  |  | 89.2957
| Say |  |  |  | 89
89
Analysis of rate
1.53 | Supplying and drawing of UTP 4 pair CAT 6 LAN Cable in the existing surface/ recessed steel/ PVC conduit as required.
| UTP 4 Pair CAT 6 LAN Cable |  | DSR | Rate Rs. | 34
COST FOR 50 METERS
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1451 | UTP 4 Pair CAT 6 LAN Cable | metre | 51.5 | 20.77 | 1069.66
| Total cost of materials |  |  |  | 1069.66
| Cartage @ 1 % of A1 |  |  |  | 10.6966
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 1487.8566
| OVERHEADS & PROFIT @ 15 % |  |  |  | 223.18
| Cost for 100 Fans |  |  |  | 1711.0366
| Rate per meter |  |  |  | 34.2207
| Say |  |  |  | 34
34
CHAPTER 2 – MCCB, MCB & DB'S (Analysis of rate based on DAR)
Analysis of rate
2.1 | Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.
2.1.1 | 32 Amp TP&N |  |  | DSR Rate Rs. | 1493
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1601 | 32 amps. TPN, switch disconnector fuse unit | each | 1 | 1184 | 1184
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
2934 | Earthing thimbles and solder | L.S. | 1 | 11 | 11
| Total cost of materials |  |  |  | 1205
| Cartage @ 1 % of A1 |  |  |  | 12.05
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1298.55
| OVERHEADS & PROFIT @ 15 % |  |  |  | 194.78
| TOTAL |  |  |  | 1493.33
| Rate per Each |  |  |  | 1493.33
| Say |  |  |  | 1493
1493
Analysis of rate
2.1 | Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.
2.1.2 | 63 Amp TP&N |  |  | DSR Rate Rs. | 2110
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1602 | 63 amps. TPN, switch disconnector fuse unit | each | 1 | 1670.63 | 1670.63
2863 | 38mm X 10mm bolts & nuts | each | 4 | 7 | 28
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
2934 | Earthing thimbles and solder | L.S. | 1 | 11 | 11
| Total cost of materials |  |  |  | 1711.63
| Cartage @ 1 % of A1 |  |  |  | 17.1163
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 1834.6963
| OVERHEADS & PROFIT @ 15 % |  |  |  | 275.2
| TOTAL |  |  |  | 2109.8963
| Rate per Each |  |  |  | 2109.8963
| Say |  |  |  | 2110
2110
Analysis of rate
2.1 | Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.
2.1.3 | 100 Amp TP&N |  |  | DSR Rate Rs. | 4376
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1603 | 100 amps. TPN, switch disconnector fuse unit | each | 1 | 3621.38 | 3621.38
2863 | 38mm X 10mm bolts & nuts | each | 4 | 7 | 28
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
2934 | Earthing thimbles and solder | L.S. | 1 | 11 | 11
| Total cost of materials |  |  |  | 3662.38
| Cartage @ 1 % of A1 |  |  |  | 36.6238
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 3804.9538
| OVERHEADS & PROFIT @ 15 % |  |  |  | 570.74
| TOTAL |  |  |  | 4375.6938
| Rate per Each |  |  |  | 4375.6938
| Say |  |  |  | 4376
4376
Analysis of rate
2.1 | Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.
2.1.4 | 125 Amp TP&N |  |  | DSR Rate Rs. | 4862
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1604 | 125 amps. TPN, switch disconnector fuse unit | each | 1 | 4024 | 4024
2863 | 38mm X 10mm bolts & nuts | each | 4 | 7 | 28
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
2934 | Earthing thimbles and solder | L.S. | 1 | 11 | 11
| Total cost of materials |  |  |  | 4065
| Cartage @ 1 % of A1 |  |  |  | 40.65
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 4227.9
| OVERHEADS & PROFIT @ 15 % |  |  |  | 634.19
| TOTAL |  |  |  | 4862.09
| Rate per Each |  |  |  | 4862.09
| Say |  |  |  | 4862
4862
Analysis of rate
2.1 | Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.
2.1.5 | 160 Amp TP&N |  |  | DSR Rate Rs. | 5782
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1605 | 160 amps. TPN, switch disconnector fuse unit | each | 1 | 4816 | 4816
2863 | 38mm X 10mm bolts & nuts | each | 4 | 7 | 28
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
2934 | Earthing thimbles and solder | L.S. | 1 | 11 | 11
| Total cost of materials |  |  |  | 4857
| Cartage @ 1 % of A1 |  |  |  | 48.57
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 5027.82
| OVERHEADS & PROFIT @ 15 % |  |  |  | 754.17
| TOTAL |  |  |  | 5781.99
| Rate per Each |  |  |  | 5781.99
| Say |  |  |  | 5782
5782
Analysis of rate
2.1 | Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.
2.1.6 | 200 Amp TP&N |  |  | DSR Rate Rs. | 6618
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1606 | 200 amps. TPN switch fuse unit with ISI marked HRC fuses | each | 1 | 5520 | 5520
2863 | 38mm X 10mm bolts & nuts | each | 4 | 7 | 28
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
2934 | Earthing thimbles and solder | L.S. | 1 | 11 | 11
| Total cost of materials |  |  |  | 5561
| Cartage @ 1 % of A1 |  |  |  | 55.61
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 5755.16
| OVERHEADS & PROFIT @ 15 % |  |  |  | 863.27
| TOTAL |  |  |  | 6618.43
| Rate per Each |  |  |  | 6618.43
| Say |  |  |  | 6618
6618
Analysis of rate
2.1 | Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.
2.1.7 | 320 Amp TP&N |  |  | DSR Rate Rs. | 10541
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1607 | 315 amps. TPN switch fuse unit with ISI marked HRC fuses | each | 1 | 8872.88 | 8872.88
2863 | 38mm X 10mm bolts & nuts | each | 4 | 7 | 28
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
2934 | Earthing thimbles and solder | L.S. | 1 | 11 | 11
| Total cost of materials |  |  |  | 8913.88
| Cartage @ 1 % of A1 |  |  |  | 89.1388
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 9166.0188
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1374.9
| TOTAL |  |  |  | 10540.9188
| Rate per Each |  |  |  | 10540.9188
| Say |  |  |  | 10541
10541
Analysis of rate
2.1 | Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.
2.1.8 | 400 Amp TP&N |  |  | DSR Rate Rs. | 12889
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1608 | 400 amps. TPN switch fuse unit with ISI marked HRC fuses | each | 1 | 10854 | 10854
2863 | 38mm X 10mm bolts & nuts | each | 4 | 7 | 28
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
2934 | Earthing thimbles and solder | L.S. | 1 | 11 | 11
| Total cost of materials |  |  |  | 10895
| Cartage @ 1 % of A1 |  |  |  | 108.95
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 11207.7
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1681.16
| TOTAL |  |  |  | 12888.86
| Rate per Each |  |  |  | 12888.86
| Say |  |  |  | 12889
12889
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.1 | 100 Amp, 16 KA |  |  | DSR Rate Rs. | 3218
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1610 | 3 pole MCCB, 100A, 16KA | each | 1 | 2656 | 2656
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 2666
| Cartage @ 1 % of A1 |  |  |  | 26.66
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 2798.61
| OVERHEADS & PROFIT @ 15 % |  |  |  | 419.79
| TOTAL |  |  |  | 3218.4
| Rate per Each |  |  |  | 3218.4
| Say |  |  |  | 3218
3218
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.2 | 125 Amp, 16 KA |  |  | DSR Rate Rs. | 3613
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1611 | 3 pole MCCB, 125A, 16KA | each | 1 | 2979.9 | 2979.9
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 2989.9
| Cartage @ 1 % of A1 |  |  |  | 29.899
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 3142.049
| OVERHEADS & PROFIT @ 15 % |  |  |  | 471.31
| TOTAL |  |  |  | 3613.359
| Rate per Each |  |  |  | 3613.359
| Say |  |  |  | 3613
3613
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.3 | 160 Amp, 16 KA |  |  | DSR Rate Rs. | 4096
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1612 | 3 pole MCCB, 150A, 16KA | each | 1 | 3395.7 | 3395.7
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 3405.7
| Cartage @ 1 % of A1 |  |  |  | 34.057
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 3562.007
| OVERHEADS & PROFIT @ 15 % |  |  |  | 534.3
| TOTAL |  |  |  | 4096.307
| Rate per Each |  |  |  | 4096.307
| Say |  |  |  | 4096
4096
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.4 | 200 Amp, 16 KA |  |  | DSR Rate Rs. | 5535
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1613 | 3 pole MCCB, 200A, 16KA | each | 1 | 4617.9 | 4617.9
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 4627.9
| Cartage @ 1 % of A1 |  |  |  | 46.279
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 4812.729
| OVERHEADS & PROFIT @ 15 % |  |  |  | 721.91
| TOTAL |  |  |  | 5534.639
| Rate per Each |  |  |  | 5534.639
| Say |  |  |  | 5535
5535
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.5 | 200 Amp, 25 KA |  |  | DSR Rate Rs. | 7964
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1614 | 3 pole MCCB, 200A, 25KA | each | 1 | 6709.5 | 6709.5
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 6719.5
| Cartage @ 1 % of A1 |  |  |  | 67.195
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 6925.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1038.79
| TOTAL |  |  |  | 7964.035
| Rate per Each |  |  |  | 7964.035
| Say |  |  |  | 7964
7964
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.6 | 250 Amp, 25 KA |  |  | DSR Rate Rs. | 9397
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1615 | 3 pole MCCB, 250A, 25KA | each | 1 | 7934.85 | 7934.85
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 7944.85
| Cartage @ 1 % of A1 |  |  |  | 79.4485
LABOUR
1001 | Wireman | day | 0.18 | 447 | 80.46
1007 | Khallasi | day | 0.18 | 368 | 66.24
| TOTAL |  |  |  | 8170.9985
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1225.65
| TOTAL |  |  |  | 9396.6485
| Rate per Each |  |  |  | 9396.6485
| Say |  |  |  | 9397
9397
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.7 | 250 Amp, 35 KA |  |  | DSR Rate Rs. | 10176
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1616 | 3 pole MCCB, 250A, 35KA | each | 1 | 8605.8 | 8605.8
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 8615.8
| Cartage @ 1 % of A1 |  |  |  | 86.158
LABOUR
1001 | Wireman | day | 0.18 | 447 | 80.46
1007 | Khallasi | day | 0.18 | 368 | 66.24
| TOTAL |  |  |  | 8848.658
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1327.3
| TOTAL |  |  |  | 10175.958
| Rate per Each |  |  |  | 10175.958
| Say |  |  |  | 10176
10176
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.8 | 315 Amp, 35 KA |  |  | DSR Rate Rs. | 15672
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1617 | 3 pole MCCB, 315A, 35KA | each | 1 | 13321.35 | 13321.35
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 13331.35
| Cartage @ 1 % of A1 |  |  |  | 133.3135
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 13627.6635
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2044.15
| TOTAL |  |  |  | 15671.8135
| Rate per Each |  |  |  | 15671.8135
| Say |  |  |  | 15672
15672
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.9 | 400 Amp, 35 KA |  |  | DSR Rate Rs. | 15672
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1618 | 3 pole MCCB, 400A, 35KA | each | 1 | 13321.35 | 13321.35
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 13331.35
| Cartage @ 1 % of A1 |  |  |  | 133.3135
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 13627.6635
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2044.15
| TOTAL |  |  |  | 15671.8135
| Rate per Each |  |  |  | 15671.8135
| Say |  |  |  | 15672
15672
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.10 | 500 Amp, 35 KA |  |  | DSR Rate Rs. | 18163
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1619 | 3 pole MCCB, 500A, 35KA | each | 1 | 15425.55 | 15425.55
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 15435.55
| Cartage @ 1 % of A1 |  |  |  | 154.3555
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 15793.6555
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2369.05
| TOTAL |  |  |  | 18162.7055
| Rate per Each |  |  |  | 18162.7055
| Say |  |  |  | 18163
18163
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.11 | 630 Amp, 50 KA |  |  | DSR Rate Rs. | 20234
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1620 | 3 pole MCCB, 630A, 50KA | each | 1 | 17208.45 | 17208.45
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 17218.45
| Cartage @ 1 % of A1 |  |  |  | 172.1845
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 17594.3845
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2639.16
| TOTAL |  |  |  | 20233.5445
| Rate per Each |  |  |  | 20233.5445
| Say |  |  |  | 20234
20234
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.12 | 800 Amp, 50 KA |  |  | DSR Rate Rs. | 24679
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1621 | 3 pole MCCB, 800A, 50KA | each | 1 | 21035.7 | 21035.7
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 21045.7
| Cartage @ 1 % of A1 |  |  |  | 210.457
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 21459.907
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3218.99
| TOTAL |  |  |  | 24678.897
| Rate per Each |  |  |  | 24678.897
| Say |  |  |  | 24679
24679
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.13 | 100 Amp, 30 KA |  |  | DSR Rate Rs. | 5360
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1622 | 4 pole MCCB,100A,30KA | each | 1 | 4500 | 4500
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 4510
| Cartage @ 1 % of A1 |  |  |  | 45.1
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 4661.05
| OVERHEADS & PROFIT @ 15 % |  |  |  | 699.16
| TOTAL |  |  |  | 5360.21
| Rate per Each |  |  |  | 5360.21
| Say |  |  |  | 5360
5360
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.14 | 125 Amp, 36KA, FPMCCB |  |  | DSR Rate Rs. | 5449
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1623 | 4 pole MCCB, 125A, 36KA | each | 1 | 4560 | 4560
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 4570
| Cartage @ 1 % of A1 |  |  |  | 45.7
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 4737.95
| OVERHEADS & PROFIT @ 15 % |  |  |  | 710.69
| TOTAL |  |  |  | 5448.64
| Rate per Each |  |  |  | 5448.64
| Say |  |  |  | 5449
5449
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.15 | 200 Amp, 36KA, FPMCCB |  |  | DSR Rate Rs. | 13133
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1624 | 4 pole MCCB, 200A, 36KA | each | 1 | 11176 | 11176
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 11186
| Cartage @ 1 % of A1 |  |  |  | 111.86
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 11420.11
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1713.02
| TOTAL |  |  |  | 13133.13
| Rate per Each |  |  |  | 13133.13
| Say |  |  |  | 13133
13133
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.16 | 250 Amp, 36KA, FPMCCB |  |  | DSR Rate Rs. | 14660
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1625 | 4 pole MCCB,250A, 36KA | each | 1 | 12474 | 12474
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 12484
| Cartage @ 1 % of A1 |  |  |  | 124.84
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 12747.39
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1912.11
| TOTAL |  |  |  | 14659.5
| Rate per Each |  |  |  | 14659.5
| Say |  |  |  | 14660
14660
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.17 | 250 Amp, 50KA, FPMCCB |  |  | DSR Rate Rs. | 13694
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1626 | 4 pole MCCB,250A, 50KA | each | 1 | 11642.4 | 11642.4
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 11652.4
| Cartage @ 1 % of A1 |  |  |  | 116.524
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 11907.474
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1786.12
| TOTAL |  |  |  | 13693.594
| Rate per Each |  |  |  | 13693.594
| Say |  |  |  | 13694
13694
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.18 | 400 Amp, 50KA, FPMCCB |  |  | DSR Rate Rs. | 19089
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1627 | 4 pole MCCB,400A, 50KA | each | 1 | 16279.2 | 16279.2
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 16289.2
| Cartage @ 1 % of A1 |  |  |  | 162.892
LABOUR
1001 | Wireman | day | 0.18 | 447 | 80.46
1007 | Khallasi | day | 0.18 | 368 | 66.24
| TOTAL |  |  |  | 16598.792
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2489.82
| TOTAL |  |  |  | 19088.612
| Rate per Each |  |  |  | 19088.612
| Say |  |  |  | 19089
19089
Analysis of rate
2.2 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
2.2.19 | 630 Amp, 50KA, FPMCCB |  |  | DSR Rate Rs. | 23710
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1628 | 4 pole MCCB,630A, 50KA | each | 1 | 20257.65 | 20257.65
2861 | 25mm X 3mm bolts & nuts | each | 4 | 2 | 8
2859 | Rubber/ PVC bushes | each | 4 | 0.5 | 2
| Total cost of materials |  |  |  | 20267.65
| Cartage @ 1 % of A1 |  |  |  | 202.6765
LABOUR
1001 | Wireman | day | 0.18 | 447 | 80.46
1007 | Khallasi | day | 0.18 | 368 | 66.24
| TOTAL |  |  |  | 20617.0265
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3092.55
| TOTAL |  |  |  | 23709.5765
| Rate per Each |  |  |  | 23709.5765
| Say |  |  |  | 23710
23710
Analysis of rate
2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.3.1 | 2 + 4 way, Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1734 | 2+4 way / 6 Way , SPN, single door, MCB DB | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 182.945
| OVERHEADS & PROFIT @ 15 % |  |  |  | 27.44
| TOTAL |  |  |  | 210.385
| Rate per Each |  |  |  | 210.385
| Say |  |  |  | 210
210
Analysis of rate
2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.3.2 | 2 + 6 way, Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1735 | 2+6 way / 10 Way, SPN, single door, MCB DB | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 182.945
| OVERHEADS & PROFIT @ 15 % |  |  |  | 27.44
| TOTAL |  |  |  | 210.385
| Rate per Each |  |  |  | 210.385
| Say |  |  |  | 210
210
Analysis of rate
2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.3.3 | 2 + 8 way, Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1736 | 2+8 way / 14 Way, SPN, single door, MCB DB | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 182.945
| OVERHEADS & PROFIT @ 15 % |  |  |  | 27.44
| TOTAL |  |  |  | 210.385
| Rate per Each |  |  |  | 210.385
| Say |  |  |  | 210
210
Analysis of rate
2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.3.4 | 2 + 12 way, Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1737 | 2+12 way / 14 Way, SPN, single door, MCB DB | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 182.945
| OVERHEADS & PROFIT @ 15 % |  |  |  | 27.44
| TOTAL |  |  |  | 210.385
| Rate per Each |  |  |  | 210.385
| Say |  |  |  | 210
210
Analysis of rate
2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.3.5 | 2 + 4 way, Double door |  |  | DSR Rate Rs. | 942
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1738 | 6 Way, SPN, double door, MCB DB | each | 1 | 630 | 630
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 654.5
| Cartage @ 1 % of A1 |  |  |  | 6.545
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 819.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 122.89
| TOTAL |  |  |  | 942.135
| Rate per Each |  |  |  | 942.135
| Say |  |  |  | 942
942
Analysis of rate
2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.3.6 | 2 + 6 way, Double door |  |  | DSR Rate Rs. | 1061
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1739 | 8 Way, SPN, double door, MCB DB | each | 1 | 732 | 732
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 756.5
| Cartage @ 1 % of A1 |  |  |  | 7.565
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 922.265
| OVERHEADS & PROFIT @ 15 % |  |  |  | 138.34
| TOTAL |  |  |  | 1060.605
| Rate per Each |  |  |  | 1060.605
| Say |  |  |  | 1061
1061
Analysis of rate
2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.3.7 | 2 + 8 way, Double door |  |  | DSR Rate Rs. | 1151
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1740 | 12 Way, SPN, double door, MCB DB | each | 1 | 810 | 810
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 834.5
| Cartage @ 1 % of A1 |  |  |  | 8.345
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 1001.045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 150.16
| TOTAL |  |  |  | 1151.205
| Rate per Each |  |  |  | 1151.205
| Say |  |  |  | 1151
1151
Analysis of rate
2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.3.8 | 2 + 12 way, Double door |  |  | DSR Rate Rs. | 1364
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1741 | 14 Way, SPN, double door, MCB DB | each | 1 | 993 | 993
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 1017.5
| Cartage @ 1 % of A1 |  |  |  | 10.175
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 1185.875
| OVERHEADS & PROFIT @ 15 % |  |  |  | 177.88
| TOTAL |  |  |  | 1363.755
| Rate per Each |  |  |  | 1363.755
| Say |  |  |  | 1364
1364
Analysis of rate
2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.4.1 | 4 way (4 + 12), Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1751 | 4 way (4+12), TPN, MCB DB, single door, horizontal type | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 215.545
| OVERHEADS & PROFIT @ 15 % |  |  |  | 32.33
| TOTAL |  |  |  | 247.875
| Rate per Each |  |  |  | 247.875
| Say |  |  |  | 248
248
Analysis of rate
2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.4.2 | 6 way (4 + 18), Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1752 | 6 way (4+18), TPN, MCB DB, single door, horizontal type | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 215.545
| OVERHEADS & PROFIT @ 15 % |  |  |  | 32.33
| TOTAL |  |  |  | 247.875
| Rate per Each |  |  |  | 247.875
| Say |  |  |  | 248
248
Analysis of rate
2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.4.3 | 8 way (4 + 24), Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1753 | 8 way (4+24), TPN, MCB DB, single door, horizontal type | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 215.545
| OVERHEADS & PROFIT @ 15 % |  |  |  | 32.33
| TOTAL |  |  |  | 247.875
| Rate per Each |  |  |  | 247.875
| Say |  |  |  | 248
248
Analysis of rate
2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.4.4 | 4 way (4 + 12), Double door |  |  | DSR Rate Rs. | 2198
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1754 | 4 way (4+12), TPN, MCB DB, double door, horizontal type | each | 1 | 1679.4 | 1679.4
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 1703.9
| Cartage @ 1 % of A1 |  |  |  | 17.039
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 1911.739
| OVERHEADS & PROFIT @ 15 % |  |  |  | 286.76
| TOTAL |  |  |  | 2198.499
| Rate per Each |  |  |  | 2198.499
| Say |  |  |  | 2198
2198
Analysis of rate
2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.4.5 | 6 way (4 + 18), Double door |  |  | DSR Rate Rs. | 2659
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1755 | 6 way (4+18), TPN, MCB DB, double door, horizontal type | each | 1 | 2076 | 2076
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 2100.5
| Cartage @ 1 % of A1 |  |  |  | 21.005
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 2312.305
| OVERHEADS & PROFIT @ 15 % |  |  |  | 346.85
| TOTAL |  |  |  | 2659.155
| Rate per Each |  |  |  | 2659.155
| Say |  |  |  | 2659
2659
Analysis of rate
2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
2.4.6 | 8 way (4 + 24), Double door |  |  | DSR Rate Rs. | 3171
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1756 | 8 way (4+24), TPN, MCB DB, double door, horizontal type | each | 1 | 2517 | 2517
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 2541.5
| Cartage @ 1 % of A1 |  |  |  | 25.415
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 2757.715
| OVERHEADS & PROFIT @ 15 % |  |  |  | 413.66
| TOTAL |  |  |  | 3171.375
| Rate per Each |  |  |  | 3171.375
| Say |  |  |  | 3171
3171
Analysis of rate
2.5 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.5.1 | 4 way (4 + 12), Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1757 | 4 way (4+12), TPN, vertical type, MCB DB, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 215.545
| OVERHEADS & PROFIT @ 15 % |  |  |  | 32.33
| TOTAL |  |  |  | 247.875
| Rate per Each |  |  |  | 247.875
| Say |  |  |  | 248
248
Analysis of rate
2.5 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.5.2 | 8 way (4 + 24), Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1758 | 8 way (4+24), TPN, vertical type, MCB DB, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 215.545
| OVERHEADS & PROFIT @ 15 % |  |  |  | 32.33
| TOTAL |  |  |  | 247.875
| Rate per Each |  |  |  | 247.875
| Say |  |  |  | 248
248
Analysis of rate
2.5 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.5.3 | 12 way (4 + 36), Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1759 | 12 way (4+36), TPN, vertical type, MCB DB, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 215.545
| OVERHEADS & PROFIT @ 15 % |  |  |  | 32.33
| TOTAL |  |  |  | 247.875
| Rate per Each |  |  |  | 247.875
| Say |  |  |  | 248
248
Analysis of rate
2.5 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.5.4 | 4 way (4 + 12), Double door |  |  | DSR Rate Rs. | 4502
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1760 | 4 way (4+12), TPN, vertical type, MCB DB, double door | each | 1 | 3662.51 | 3662.51
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 3687.01
| Cartage @ 1 % of A1 |  |  |  | 36.8701
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 3914.6801
| OVERHEADS & PROFIT @ 15 % |  |  |  | 587.2
| TOTAL |  |  |  | 4501.8801
| Rate per Each |  |  |  | 4501.8801
| Say |  |  |  | 4502
4502
Analysis of rate
2.5 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.5.5 | 8 way (4 + 24), Double door |  |  | DSR Rate Rs. | 5664
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1761 | 8 way (4+24), TPN, vertical type, MCB DB, double door | each | 1 | 4663.02 | 4663.02
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 4687.52
| Cartage @ 1 % of A1 |  |  |  | 46.8752
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 4925.1952
| OVERHEADS & PROFIT @ 15 % |  |  |  | 738.78
| TOTAL |  |  |  | 5663.9752
| Rate per Each |  |  |  | 5663.9752
| Say |  |  |  | 5664
5664
Analysis of rate
2.5 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.5.6 | 12 way (4 + 36), Double door |  |  | DSR Rate Rs. | 7189
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1762 | 12 way (4+36), TPN, vertical type, MCB DB, double door | each | 1 | 5975.82 | 5975.82
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 6000.32
| Cartage @ 1 % of A1 |  |  |  | 60.0032
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 6251.1232
| OVERHEADS & PROFIT @ 15 % |  |  |  | 937.67
| TOTAL |  |  |  | 7188.7932
| Rate per Each |  |  |  | 7188.7932
| Say |  |  |  | 7189
7189
Analysis of rate
2.6 | Supplying and fixing following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, with provision of 100 amps TP 16 KA MCCB as incomer, interconnection between incomer MCCB and bus bars (but without MCB's/ MCCB) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.6.1 | 4 Way TP |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1763 | 4 way, TPN, vertical type, single door, MCB DB with provision to mount MCCB as incomer. | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 215.545
| OVERHEADS & PROFIT @ 15 % |  |  |  | 32.33
| TOTAL |  |  |  | 247.875
| Rate per Each |  |  |  | 247.875
| Say |  |  |  | 248
248
Analysis of rate
2.6 | Supplying and fixing following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, with provision of 100 amps TP 16 KA MCCB as incomer, interconnection between incomer MCCB and bus bars (but without MCB's/ MCCB) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.6.2 | 8 Way TP |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1764 | 8 way, TPN, vertical type, single door, MCB DB with provision to mount MCCB as incomer. | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 215.545
| OVERHEADS & PROFIT @ 15 % |  |  |  | 32.33
| TOTAL |  |  |  | 247.875
| Rate per Each |  |  |  | 247.875
| Say |  |  |  | 248
248
Analysis of rate
2.6 | Supplying and fixing following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, with provision of 100 amps TP 16 KA MCCB as incomer, interconnection between incomer MCCB and bus bars (but without MCB's/ MCCB) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.6.3 | 12 Way TP |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1765 | 12 way, TPN, vertical type, single door, MCB DB with provision to mount MCCB as incomer. | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.12 | 447 | 53.64
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.24 | 368 | 88.32
| TOTAL |  |  |  | 215.545
| OVERHEADS & PROFIT @ 15 % |  |  |  | 32.33
| TOTAL |  |  |  | 247.875
| Rate per Each |  |  |  | 247.875
| Say |  |  |  | 248
248
Analysis of rate
2.7 | Supplying and fixing following way prewired SP&N MCB distribution board of steel sheet for 240 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator)
2.7.1 | 2 + 4 way, Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1771 | 2 + 4 way, SPN, prewired MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 222.495
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.37
| TOTAL |  |  |  | 255.865
| Rate per Each |  |  |  | 255.865
| Say |  |  |  | 256
256
Analysis of rate
2.7 | Supplying and fixing following way prewired SP&N MCB distribution board of steel sheet for 240 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator)
2.7.2 | 2 + 8 way, Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1772 | 2 + 8 way, SPN, prewired MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 222.495
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.37
| TOTAL |  |  |  | 255.865
| Rate per Each |  |  |  | 255.865
| Say |  |  |  | 256
256
Analysis of rate
2.7 | Supplying and fixing following way prewired SP&N MCB distribution board of steel sheet for 240 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator)
2.7.3 | 2 + 12 way, Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1773 | 2 + 12 way, SPN, prewired MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 222.495
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.37
| TOTAL |  |  |  | 255.865
| Rate per Each |  |  |  | 255.865
| Say |  |  |  | 256
256
Analysis of rate
2.7 | Supplying and fixing following way prewired SP&N MCB distribution board of steel sheet for 240 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator)
2.7.4 | 2 + 4 way, Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1774 | 2 + 4 way, SPN, prewired MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 222.495
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.37
| TOTAL |  |  |  | 255.865
| Rate per Each |  |  |  | 255.865
| Say |  |  |  | 256
256
Analysis of rate
2.7 | Supplying and fixing following way prewired SP&N MCB distribution board of steel sheet for 240 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator)
2.7.5 | 2 + 8 way, Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1775 | 2 + 8 way, SPN, prewired MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 222.495
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.37
| TOTAL |  |  |  | 255.865
| Rate per Each |  |  |  | 255.865
| Say |  |  |  | 256
256
Analysis of rate
2.7 | Supplying and fixing following way prewired SP&N MCB distribution board of steel sheet for 240 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator)
2.7.6 | 2 + 12 way, Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1776 | 2 + 12 way, SPN, prewired MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 222.495
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.37
| TOTAL |  |  |  | 255.865
| Rate per Each |  |  |  | 255.865
| Say |  |  |  | 256
256
Analysis of rate
2.8 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
2.8.1 | 4 way (4 + 12), Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1779 | 4 way, (4+12) TPN, prewired MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.8 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
2.8.2 | 6 way (4 + 18), Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1780 | 6 way, (4+18) TPN, prewired MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.8 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
2.8.3 | 8 way (4 + 24), Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1781 | 8 way, (4+24) TPN, prewired MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.8 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
2.8.4 | 12 way (4 + 36), Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1782 | 12 way, (4+36) TPN, prewired MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.8 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
2.8.5 | 4 way (4 + 12), Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1783 | 4 way, (4+12) TPN, prewired MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.8 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
2.8.6 | 6 way (4 + 18), Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1784 | 6 way, (4+18) TPN, prewired MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.8 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
2.8.7 | 8 way (4 + 24), Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1785 | 8 way, (4+24) TPN, prewired MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.8 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
2.8.8 | 12 way (4 + 36), Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1786 | 12 way, (4+36) TPN, prewired MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.9 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.9.1 | 4 way Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1787 | 4 way (4+4), TPN, vertical type, prewired, MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.9 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.9.2 | 6 way Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1788 | 6 way (4+6), TPN, vertical type, prewired, MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.9 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.9.3 | 8 way Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1789 | 8 way (4+8), TPN, vertical type, prewired, MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.9 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.9.4 | 12 way Single door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1790 | 12 way (4+12), TPN, vertical type, prewired, MCB DB with extended loose wire box, single door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.9 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.9.5 | 4 way Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1791 | 4 way (4+4), TPN, vertical type, prewired, MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.9 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.9.6 | 6 way Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1792 | 6 way (4+6), TPN, vertical type, prewired, MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.9 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.9.7 | 8 way Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1793 | 8 way (4+8), TPN, vertical type, prewired, MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.9 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.9.8 | 12 way Double door |  |  | DSR Rate Rs. | 0
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1794 | 12 way (4+12), TPN, vertical type, prewired, MCB DB with extended loose wire box, double door | each | 1 | 0 | 0
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 24.5
| Cartage @ 1 % of A1 |  |  |  | 0.245
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1010 | Mason, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 263.245
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.49
| TOTAL |  |  |  | 302.735
| Rate per Each |  |  |  | 302.735
| Say |  |  |  | 303
303
Analysis of rate
2.10 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.10.1 | Single pole |  |  | DSR Rate Rs. | 173
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1706 | 6 amps. to 32 amps. ratings , SP MCB, "C" curve, 10 KA breaking capacity | each | 1 | 117 | 117
| Total cost of materials |  |  |  | 117
| Cartage @ 1 % of A1 |  |  |  | 1.17
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 150.77
| OVERHEADS & PROFIT @ 15 % |  |  |  | 22.62
| TOTAL |  |  |  | 173.39
| Rate per Each |  |  |  | 173.39
| Say |  |  |  | 173
173
Analysis of rate
2.10 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.10.2 | Single pole and neutral |  |  | DSR Rate Rs. | 445
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1707 | 6 amps. to 32 amps. ratings , SPN MCB, "C" curve, 10 KA breaking capacity | each | 1 | 351 | 351
| Total cost of materials |  |  |  | 351
| Cartage @ 1 % of A1 |  |  |  | 3.51
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 387.11
| OVERHEADS & PROFIT @ 15 % |  |  |  | 58.07
| TOTAL |  |  |  | 445.18
| Rate per Each |  |  |  | 445.18
| Say |  |  |  | 445
445
Analysis of rate
2.10 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.10.3 | Double pole |  |  | DSR Rate Rs. | 463
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1708 | 6 amps. to 32 amps. ratings , DP MCB, "C" curve, 10 KA breaking capacity | each | 1 | 366 | 366
| Total cost of materials |  |  |  | 366
| Cartage @ 1 % of A1 |  |  |  | 3.66
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 402.26
| OVERHEADS & PROFIT @ 15 % |  |  |  | 60.34
| TOTAL |  |  |  | 462.6
| Rate per Each |  |  |  | 462.6
| Say |  |  |  | 463
463
Analysis of rate
2.10 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.10.4 | Triple pole |  |  | DSR Rate Rs. | 700
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1709 | 6 amps. to 32 amps. ratings , TP MCB, "C" curve, 10 KA breaking capacity | each | 1 | 570 | 570
| Total cost of materials |  |  |  | 570
| Cartage @ 1 % of A1 |  |  |  | 5.7
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 608.3
| OVERHEADS & PROFIT @ 15 % |  |  |  | 91.25
| TOTAL |  |  |  | 699.55
| Rate per Each |  |  |  | 699.55
| Say |  |  |  | 700
700
Analysis of rate
2.10 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.10.5 | Triple pole and neutral |  |  | DSR Rate Rs. | 891
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1710 | 6 amps. to 32 amps. ratings , TPN MCB, "C" curve, 10 KA breaking capacity | each | 1 | 735 | 735
| Total cost of materials |  |  |  | 735
| Cartage @ 1 % of A1 |  |  |  | 7.35
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 774.95
| OVERHEADS & PROFIT @ 15 % |  |  |  | 116.24
| TOTAL |  |  |  | 891.19
| Rate per Each |  |  |  | 891.19
| Say |  |  |  | 891
891
Analysis of rate
2.11 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required.
|  |  |  | DSR Rate Rs. | 7
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1711 | Single pole, blanking plate | each | 1 | 5 | 5
| Total cost of materials |  |  |  | 5
| Cartage @ 1 % of A1 |  |  |  | 0.05
LABOUR
1001 | Wireman | day | 0.001 | 447 | 0.45
1007 | Khallasi | day | 0.001 | 368 | 0.37
| TOTAL |  |  |  | 5.87
| OVERHEADS & PROFIT @ 15 % |  |  |  | 0.88
| TOTAL |  |  |  | 6.75
| Rate per Each |  |  |  | 6.75
| Say |  |  |  | 7
7
Analysis of rate
2.12 | Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.12.1 | 40 amps |  |  | DSR Rate Rs. | 222
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1712 | 40 amps., 2 pole isolator | each | 1 | 159 | 159
| Total cost of materials |  |  |  | 159
| Cartage @ 1 % of A1 |  |  |  | 1.59
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 193.19
| OVERHEADS & PROFIT @ 15 % |  |  |  | 28.98
| TOTAL |  |  |  | 222.17
| Rate per Each |  |  |  | 222.17
| Say |  |  |  | 222
222
Analysis of rate
2.12 | Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.12.2 | 63 amps |  |  | DSR Rate Rs. | 254
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1713 | 63 amps., 2 pole isolator | each | 1 | 186 | 186
| Total cost of materials |  |  |  | 186
| Cartage @ 1 % of A1 |  |  |  | 1.86
LABOUR
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 220.46
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.07
| TOTAL |  |  |  | 253.53
| Rate per Each |  |  |  | 253.53
| Say |  |  |  | 254
254
Analysis of rate
2.13 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.13.1 | 40 amps |  |  | DSR Rate Rs. | 667
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1714 | 40 amps., 4 pole isolator | each | 1 | 510 | 510
| Total cost of materials |  |  |  | 510
| Cartage @ 1 % of A1 |  |  |  | 5.1
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 580.3
| OVERHEADS & PROFIT @ 15 % |  |  |  | 87.05
| TOTAL |  |  |  | 667.35
| Rate per Each |  |  |  | 667.35
| Say |  |  |  | 667
667
Analysis of rate
2.13 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.13.2 | 63 amps |  |  | DSR Rate Rs. | 678
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1715 | 63 amps., 4 pole isolator | each | 1 | 519 | 519
| Total cost of materials |  |  |  | 519
| Cartage @ 1 % of A1 |  |  |  | 5.19
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 589.39
| OVERHEADS & PROFIT @ 15 % |  |  |  | 88.41
| TOTAL |  |  |  | 677.8
| Rate per Each |  |  |  | 677.8
| Say |  |  |  | 678
678
Analysis of rate
2.13 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.13.3 | 100 amps |  |  | DSR Rate Rs. | 859
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1716 | 100 amps., 4 pole isolator | each | 1 | 675 | 675
| Total cost of materials |  |  |  | 675
| Cartage @ 1 % of A1 |  |  |  | 6.75
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 746.95
| OVERHEADS & PROFIT @ 15 % |  |  |  | 112.04
| TOTAL |  |  |  | 858.99
| Rate per Each |  |  |  | 858.99
| Say |  |  |  | 859
859
Analysis of rate
2.14 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.14.1 | 25 amps |  |  | DSR Rate Rs. | 1650
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1717 | 25 amps. rating, 2 pole RCCB, 100mA/ 300mA | each | 1 | 1380 | 1380
| Total cost of materials |  |  |  | 1380
| Cartage @ 1 % of A1 |  |  |  | 13.8
LABOUR
1001 | Wireman | day | 0.05 | 447 | 22.35
1007 | Khallasi | day | 0.05 | 368 | 18.4
| TOTAL |  |  |  | 1434.55
| OVERHEADS & PROFIT @ 15 % |  |  |  | 215.18
| TOTAL |  |  |  | 1649.73
| Rate per Each |  |  |  | 1649.73
| Say |  |  |  | 1650
1650
Analysis of rate
2.14 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.14.2 | 40 amps |  |  | DSR Rate Rs. | 1719
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1718 | 40 amps. rating, 2 pole RCCB, 100mA/ 300mA | each | 1 | 1440 | 1440
| Total cost of materials |  |  |  | 1440
| Cartage @ 1 % of A1 |  |  |  | 14.4
LABOUR
1001 | Wireman | day | 0.05 | 447 | 22.35
1007 | Khallasi | day | 0.05 | 368 | 18.4
| TOTAL |  |  |  | 1495.15
| OVERHEADS & PROFIT @ 15 % |  |  |  | 224.27
| TOTAL |  |  |  | 1719.42
| Rate per Each |  |  |  | 1719.42
| Say |  |  |  | 1719
1719
Analysis of rate
2.14 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.14.3 | 63 amps |  |  | DSR Rate Rs. | 2242
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1719 | 63 amps. rating, 2 pole RCCB, 100mA/ 300mA | each | 1 | 1890 | 1890
| Total cost of materials |  |  |  | 1890
| Cartage @ 1 % of A1 |  |  |  | 18.9
LABOUR
1001 | Wireman | day | 0.05 | 447 | 22.35
1007 | Khallasi | day | 0.05 | 368 | 18.4
| TOTAL |  |  |  | 1949.65
| OVERHEADS & PROFIT @ 15 % |  |  |  | 292.45
| TOTAL |  |  |  | 2242.1
| Rate per Each |  |  |  | 2242.1
| Say |  |  |  | 2242
2242
Analysis of rate
2.15 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.15.1 | 25 amps |  |  | DSR Rate Rs. | 2096
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1720 | 25 amps. rating, 4 pole RCCB, 100mA/ 300mA | each | 1 | 1740 | 1740
| Total cost of materials |  |  |  | 1740
| Cartage @ 1 % of A1 |  |  |  | 17.4
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 1822.6
| OVERHEADS & PROFIT @ 15 % |  |  |  | 273.39
| TOTAL |  |  |  | 2095.99
| Rate per Each |  |  |  | 2095.99
| Say |  |  |  | 2096
2096
Analysis of rate
2.15 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.15.2 | 40 amps |  |  | DSR Rate Rs. | 2131
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1721 | 40 amps. rating, 4 pole RCCB, 100mA/ 300mA | each | 1 | 1770 | 1770
| Total cost of materials |  |  |  | 1770
| Cartage @ 1 % of A1 |  |  |  | 17.7
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 1852.9
| OVERHEADS & PROFIT @ 15 % |  |  |  | 277.94
| TOTAL |  |  |  | 2130.84
| Rate per Each |  |  |  | 2130.84
| Say |  |  |  | 2131
2131
Analysis of rate
2.15 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
2.15.3 | 63 amps |  |  | DSR Rate Rs. | 2302
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1722 | 63 amps. rating, 4 pole RCCB, 100mA/ 300mA | each | 1 | 1917 | 1917
| Total cost of materials |  |  |  | 1917
| Cartage @ 1 % of A1 |  |  |  | 19.17
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 2001.37
| OVERHEADS & PROFIT @ 15 % |  |  |  | 300.21
| TOTAL |  |  |  | 2301.58
| Rate per Each |  |  |  | 2301.58
| Say |  |  |  | 2302
2302
Analysis of rate
2.16 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32amps 240 volts "C" curve DP MCB complete with connections, testing and commissioning etc. as required.
|  |  |  | DSR Rate Rs. | 627
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1742 | Sheet steel DP MCB enclosure | each | 1 | 92.77 | 92.77
1708 | 6 amps. to 32 amps. ratings , DP MCB, "C" curve, 10 KA breaking capacity | each | 1 | 366 | 366
| Total cost of materials |  |  |  | 458.77
| Cartage @ 1 % of A1 |  |  |  | 4.5877
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 544.8577
| OVERHEADS & PROFIT @ 15 % |  |  |  | 81.73
| TOTAL |  |  |  | 626.5877
| Rate per Each |  |  |  | 626.5877
| Say |  |  |  | 627
627
Analysis of rate
2.17 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required.
|  |  |  | DSR Rate Rs. | 878
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1743 | Sheet steel TP MCB enclosure | each | 1 | 105.5 | 105.5
1709 | 6 amps. to 32 amps. ratings , TP MCB, "C" curve, 10 KA breaking capacity | each | 1 | 570 | 570
| Total cost of materials |  |  |  | 675.5
| Cartage @ 1 % of A1 |  |  |  | 6.755
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 763.755
| OVERHEADS & PROFIT @ 15 % |  |  |  | 114.56
| TOTAL |  |  |  | 878.315
| Rate per Each |  |  |  | 878.315
| Say |  |  |  | 878
878
Analysis of rate
2.18 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required.
|  |  |  | DSR Rate Rs. | 980
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1730 | 20 amps. SPN, industrial type socket outlet, with plug top and metal chained cover in sheet steel enclosure | each | 1 | 495 | 495
1706 | 6 amps. to 32 amps. ratings , SP MCB, "C" curve, 10 KA breaking capacity | each | 1 | 117 | 117
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 636.5
| Cartage @ 1 % of A1 |  |  |  | 6.365
LABOUR
1001 | Wireman | day | 0.18 | 447 | 80.46
1010 | Mason, Grade 2 | day | 0.18 | 407 | 73.26
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 851.785
| OVERHEADS & PROFIT @ 15 % |  |  |  | 127.77
| TOTAL |  |  |  | 979.555
| Rate per Each |  |  |  | 979.555
| Say |  |  |  | 980
980
Analysis of rate
2.19 | Supplying and fixing 20 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required.
|  |  |  | DSR Rate Rs. | 1455
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1731 | 20 amps. TPN, industrial type socket outlet, with plug top and metal chained cover in sheet steel enclosure | each | 1 | 535.5 | 535.5
1709 | 6 amps. to 32 amps. ratings , TP MCB, "C" curve, 10 KA breaking capacity | each | 1 | 570 | 570
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 1130
| Cartage @ 1 % of A1 |  |  |  | 11.3
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 1264.82
| OVERHEADS & PROFIT @ 15 % |  |  |  | 189.72
| TOTAL |  |  |  | 1454.54
| Rate per Each |  |  |  | 1454.54
| Say |  |  |  | 1455
1455
Analysis of rate
2.20 | Supplying and fixing 30 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 30 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required.
|  |  |  | DSR Rate Rs. | 2488
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1732 | 30 amps. TPN, industrial type socket outlet, with plug top and metal chained cover in sheet steel enclosure | each | 1 | 1425 | 1425
1709 | 6 amps. to 32 amps. ratings , TP MCB, "C" curve, 10 KA breaking capacity | each | 1 | 570 | 570
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2935 | Cement, paint, sand etc. | L.S. | 1 | 4.5 | 4.5
| Total cost of materials |  |  |  | 2019.5
| Cartage @ 1 % of A1 |  |  |  | 20.195
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 2163.215
| OVERHEADS & PROFIT @ 15 % |  |  |  | 324.48
| TOTAL |  |  |  | 2487.695
| Rate per Each |  |  |  | 2487.695
| Say |  |  |  | 2488
2488
Analysis of rate
2.21 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required.
|  |  |  | DSR Rate Rs. | 149
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2933 | 200 mm X 150 mm M.V. danger notice plate | each | 1 | 40 | 40
2865 | 15 mm long X 6 mm dia G.I. bolts and nuts | each | 6 | 4 | 24
| Total cost of materials |  |  |  | 64
| Cartage @ 1 % of A1 |  |  |  | 0.64
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 129.84
| OVERHEADS & PROFIT @ 15 % |  |  |  | 19.48
| TOTAL |  |  |  | 149.32
| Rate per Each |  |  |  | 149.32
| Say |  |  |  | 149
149
Analysis of rate
2.22 | Providing and fixing H.T. danger notice plate of 250 mm X 200 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required.
|  |  |  | DSR Rate Rs. | 163
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2932 | 250 mm X 200 mm H.T. danger notice plate | each | 1 | 52 | 52
2865 | 15 mm long X 6 mm dia G.I. bolts and nuts | each | 6 | 4 | 24
| Total cost of materials |  |  |  | 76
| Cartage @ 1 % of A1 |  |  |  | 0.76
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 141.96
| OVERHEADS & PROFIT @ 15 % |  |  |  | 21.29
| TOTAL |  |  |  | 163.25
| Rate per Each |  |  |  | 163.25
| Say |  |  |  | 163
163
CHAPTER 3 – RISING MAINS & BUS TRUNKING (Analysis of rate based on DAR)
Analysis of rate
3.1 | Supplying, installing on wall, testing and commissioning of following capacity rising mains made of 1.6mm thick sheet steel enclosure duly painted with powder coating, wall straps, fully PVC insulated 4 Nos aluminium bus bars in convenient sections and suitable for 415 volts, 3 phase, 4 wire, 50 Hz, A.C. supply with extension joints, fire proof barriers, expansion joints, thrust pads including jointing, and earthing with 2 runs of galvanised iron strips etc. as required. (Rising mains confirming to IS 8623, TEC 439)
3.1.1 | 200 amps (SC rating for 1 sec. - 15 KA) |  |  | DSR Rate Rs. | 5203
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1501 | 200 amps. TPN, rising mains in metal enclosure with aluminium busbar including fixing clamp | metre | 10 | 4213.64 | 42136.4
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 7.35 | 37.8 | 277.83
= 7x0.5m = 3.5m @ 2.1 kg/m = 7.35kg
| Total cost of materials |  |  |  | 42414.23
| Cartage @ 1 % of A1 |  |  |  | 424.1423
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 45243.3723
| OVERHEADS & PROFIT @ 15 % |  |  |  | 6786.51
| Cost for 10 Metre |  |  |  | 52029.8823
| Rate per Metre |  |  |  | 5202.9882
| Say |  |  |  | 5203
5203
Analysis of rate
3.1 | Supplying, installing on wall, testing and commissioning of following capacity rising mains made of 1.6mm thick sheet steel enclosure duly painted with powder coating, wall straps, fully PVC insulated 4 Nos aluminium bus bars in convenient sections and suitable for 415 volts, 3 phase, 4 wire, 50 Hz, A.C. supply with extension joints, fire proof barriers, expansion joints, thrust pads including jointing, and earthing with 2 runs of galvanised iron strips etc. as required. (Rising mains confirming to IS 8623, TEC 439)
3.1.2 | 315 amps (SC rating for 1 sec. - 20 KA) |  |  | DSR Rate Rs. | 5425
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1502 | 300 amps. TPN, rising mains in metal enclosure with aluminium busbar including fixing clamp | metre | 10 | 4405.17 | 44051.7
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 7.35 | 37.8 | 277.83
= 7x0.5m = 3.5m @ 2.1 kg/m = 7.35kg
| Total cost of materials |  |  |  | 44329.53
| Cartage @ 1 % of A1 |  |  |  | 443.2953
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 47177.8253
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7076.67
| Cost for 10 Metre |  |  |  | 54254.4953
| Rate per Metre |  |  |  | 5425.4495
| Say |  |  |  | 5425
5425
Analysis of rate
3.1 | Supplying, installing on wall, testing and commissioning of following capacity rising mains made of 1.6mm thick sheet steel enclosure duly painted with powder coating, wall straps, fully PVC insulated 4 Nos aluminium bus bars in convenient sections and suitable for 415 volts, 3 phase, 4 wire, 50 Hz, A.C. supply with extension joints, fire proof barriers, expansion joints, thrust pads including jointing, and earthing with 2 runs of galvanised iron strips etc. as required. (Rising mains confirming to IS 8623, TEC 439)
3.1.3 | 400 amps (SC rating for 1 sec. - 25 KA) |  |  | DSR Rate Rs. | 6672
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1503 | 400 amps. TPN, rising mains in metal enclosure with aluminium busbar including fixing clamp | metre | 10 | 5458.57 | 54585.7
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 7.35 | 37.8 | 277.83
= 7x0.5m = 3.5m @ 2.1 kg/m = 7.35kg
| Total cost of materials |  |  |  | 54863.53
| Cartage @ 1 % of A1 |  |  |  | 548.6353
LABOUR
1001 | Wireman | day | 2.25 | 447 | 1005.75
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 58020.9153
| OVERHEADS & PROFIT @ 15 % |  |  |  | 8703.14
| Cost for 10 Metre |  |  |  | 66724.0553
| Rate per Metre |  |  |  | 6672.4055
| Say |  |  |  | 6672
6672
Analysis of rate
3.1 | Supplying, installing on wall, testing and commissioning of following capacity rising mains made of 1.6mm thick sheet steel enclosure duly painted with powder coating, wall straps, fully PVC insulated 4 Nos aluminium bus bars in convenient sections and suitable for 415 volts, 3 phase, 4 wire, 50 Hz, A.C. supply with extension joints, fire proof barriers, expansion joints, thrust pads including jointing, and earthing with 2 runs of galvanised iron strips etc. as required. (Rising mains confirming to IS 8623, TEC 439)
3.1.4 | 630 amps (SC rating for 1 sec. - 45 KA) |  |  | DSR Rate Rs. | 7457
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1504 | 600 amps. TPN, rising mains in metal enclosure with aluminium busbar including fixing clamp | metre | 10 | 6128.92 | 61289.2
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 8.82 | 37.8 | 333.4
= 7x0.6m = 4.2m @ 2.1 kg/m = 8.82kg
| Total cost of materials |  |  |  | 61622.6
| Cartage @ 1 % of A1 |  |  |  | 616.226
LABOUR
1001 | Wireman | day | 2.25 | 447 | 1005.75
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 64847.576
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9727.14
| Cost for 10 Metre |  |  |  | 74574.716
| Rate per Metre |  |  |  | 7457.4716
| Say |  |  |  | 7457
7457
Analysis of rate
3.1 | Supplying, installing on wall, testing and commissioning of following capacity rising mains made of 1.6mm thick sheet steel enclosure duly painted with powder coating, wall straps, fully PVC insulated 4 Nos aluminium bus bars in convenient sections and suitable for 415 volts, 3 phase, 4 wire, 50 Hz, A.C. supply with extension joints, fire proof barriers, expansion joints, thrust pads including jointing, and earthing with 2 runs of galvanised iron strips etc. as required. (Rising mains confirming to IS 8623, TEC 439)
3.1.4 | 800 amps (SC rating for 1 sec. - 50 KA) |  |  | DSR Rate Rs. | 8983
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1505 | 800 amps. TPN, rising mains in metal enclosure with aluminium busbar including fixing clamp | metre | 10 | 7421.75 | 74217.5
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 8.82 | 37.8 | 333.4
= 7x0.6m = 4.2m @ 2.1 kg/m = 8.82kg
| Total cost of materials |  |  |  | 74550.9
| Cartage @ 1 % of A1 |  |  |  | 745.509
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 78108.909
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11716.34
| Cost for 10 Metre |  |  |  | 89825.249
| Rate per Metre |  |  |  | 8982.5249
| Say |  |  |  | 8983
8983
Analysis of rate
3.2 | Supplying, installing, testing and commissioning of following capacity TPN tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with TPN disconnector FSU and HRC fuses, connections, earthing etc. as required.
3.2.1 | 16 amps TPN |  |  | DSR Rate Rs. | 5920
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1541 | 16 amps. TPN, one way, tap off box with TPN disconnector FSU and ISI marked HRC fuses for rising mains | each | 1 | 5016.24 | 5016.24
| Total cost of materials |  |  |  | 5016.24
| Cartage @ 1 % of A1 |  |  |  | 50.1624
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 5147.9024
| OVERHEADS & PROFIT @ 15 % |  |  |  | 772.19
| TOTAL |  |  |  | 5920.0924
| Rate per Each |  |  |  | 5920.0924
| Say |  |  |  | 5920
5920
Analysis of rate
3.2 | Supplying, installing, testing and commissioning of following capacity TPN tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with TPN disconnector FSU and HRC fuses, connections, earthing etc. as required.
3.2.2 | 32 amps TPN |  |  | DSR Rate Rs. | 6238
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1542 | 32 amps. TPN, one way, tap off box with TPN disconnector FSU and ISI marked HRC fuses for rising mains | each | 1 | 5289.85 | 5289.85
| Total cost of materials |  |  |  | 5289.85
| Cartage @ 1 % of A1 |  |  |  | 52.8985
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 5424.2485
| OVERHEADS & PROFIT @ 15 % |  |  |  | 813.64
| TOTAL |  |  |  | 6237.8885
| Rate per Each |  |  |  | 6237.8885
| Say |  |  |  | 6238
6238
Analysis of rate
3.2 | Supplying, installing, testing and commissioning of following capacity TPN tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with TPN disconnector FSU and HRC fuses, connections, earthing etc. as required.
3.2.3 | 63 amps TPN |  |  | DSR Rate Rs. | 7008
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1543 | 63 amps. TPN, one way, tap off box with TPN disconnector FSU and ISI marked HRC fuses for rising mains | each | 1 | 5928.28 | 5928.28
| Total cost of materials |  |  |  | 5928.28
| Cartage @ 1 % of A1 |  |  |  | 59.2828
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 6093.5128
| OVERHEADS & PROFIT @ 15 % |  |  |  | 914.03
| TOTAL |  |  |  | 7007.5428
| Rate per Each |  |  |  | 7007.5428
| Say |  |  |  | 7008
7008
Analysis of rate
3.2 | Supplying, installing, testing and commissioning of following capacity TPN tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with TPN disconnector FSU and HRC fuses, connections, earthing etc. as required.
3.2.4 | 100 amps TPN |  |  | DSR Rate Rs. | 8067
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1544 | 100 amps. TPN, one way, tap off box with TPN disconnector FSU and ISI marked HRC fuses for rising mains | each | 1 | 6840.32 | 6840.32
| Total cost of materials |  |  |  | 6840.32
| Cartage @ 1 % of A1 |  |  |  | 68.4032
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 7014.6732
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1052.2
| TOTAL |  |  |  | 8066.8732
| Rate per Each |  |  |  | 8066.8732
| Say |  |  |  | 8067
8067
Analysis of rate
3.2 | Supplying, installing, testing and commissioning of following capacity TPN tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with TPN disconnector FSU and HRC fuses, connections, earthing etc. as required.
3.2.5 | 200 amps TPN |  |  | DSR Rate Rs. | 12660
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1545 | 200 amps. TPN, one way, tap off box with TPN disconnector FSU and ISI marked HRC fuses for rising mains | each | 1 | 10762.11 | 10762.11
| Total cost of materials |  |  |  | 10762.11
| Cartage @ 1 % of A1 |  |  |  | 107.6211
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 11008.2811
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1651.24
| TOTAL |  |  |  | 12659.5211
| Rate per Each |  |  |  | 12659.5211
| Say |  |  |  | 12660
12660
Analysis of rate
3.2 | Supplying, installing, testing and commissioning of following capacity TPN tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with TPN disconnector FSU and HRC fuses, connections, earthing etc. as required.
3.2.6 | 315 amps TPN |  |  | DSR Rate Rs. | 13401
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1546 | 315 amps. TPN, one way, tap off box with TPN disconnector FSU and ISI marked HRC fuses for rising mains | No | 1 | 11400.54 | 11400.54
| Total cost of materials |  |  |  | 11400.54
| Cartage @ 1 % of A1 |  |  |  | 114.0054
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 11653.0954
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1747.96
| TOTAL |  |  |  | 13401.0554
| Rate per Each |  |  |  | 13401.0554
| Say |  |  |  | 13401
13401
Analysis of rate
3.2 | Supplying, installing, testing and commissioning of following capacity TPN tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with TPN disconnector FSU and HRC fuses, connections, earthing etc. as required.
3.2.7 | 400 amps TPN |  |  | DSR Rate Rs. | 13931
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1547 | 400 amps. TPN, one way, tap off box with TPN disconnector FSU and ISI marked HRC fuses for rising mains | No | 1 | 11856.56 | 11856.56
| Total cost of materials |  |  |  | 11856.56
| Cartage @ 1 % of A1 |  |  |  | 118.5656
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 12113.6756
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1817.05
| TOTAL |  |  |  | 13930.7256
| Rate per Each |  |  |  | 13930.7256
| Say |  |  |  | 13931
13931
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.1 | 16 amps TPN, 2 way |  |  | DSR Rate Rs. | 8861
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1511 | 16 amps. TPN, 2 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 7524.35 | 7524.35
| Total cost of materials |  |  |  | 7524.35
| Cartage @ 1 % of A1 |  |  |  | 75.2435
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 7705.5435
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1155.83
| TOTAL |  |  |  | 8861.3735
| Rate per Each |  |  |  | 8861.3735
| Say |  |  |  | 8861
8861
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.2 | 16 amps TPN, 4 way |  |  | DSR Rate Rs. | 16542
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1512 | 16 amps. TPN, 4 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 14136.66 | 14136.66
| Total cost of materials |  |  |  | 14136.66
| Cartage @ 1 % of A1 |  |  |  | 141.3666
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 14383.9766
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2157.6
| TOTAL |  |  |  | 16541.5766
| Rate per Each |  |  |  | 16541.5766
| Say |  |  |  | 16542
16542
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.3 | 16 amps TPN, 6 way |  |  | DSR Rate Rs. | 23446
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1513 | 16 amps. TPN, 6 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 20064.95 | 20064.95
| Total cost of materials |  |  |  | 20064.95
| Cartage @ 1 % of A1 |  |  |  | 200.6495
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 20387.8495
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3058.18
| TOTAL |  |  |  | 23446.0295
| Rate per Each |  |  |  | 23446.0295
| Say |  |  |  | 23446
23446
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.4 | 16 amps TPN, 8 way |  |  | DSR Rate Rs. | 32469
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1514 | 16 amps. TPN, 8 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 27817.31 | 27817.31
| Total cost of materials |  |  |  | 27817.31
| Cartage @ 1 % of A1 |  |  |  | 278.1731
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 28234.0331
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4235.1
| TOTAL |  |  |  | 32469.1331
| Rate per Each |  |  |  | 32469.1331
| Say |  |  |  | 32469
32469
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.5 | 32 amps TPN, 2 way |  |  | DSR Rate Rs. | 9126
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1515 | 32 amps. TPN, 2 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 7752.37 | 7752.37
| Total cost of materials |  |  |  | 7752.37
| Cartage @ 1 % of A1 |  |  |  | 77.5237
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 7935.8437
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1190.38
| TOTAL |  |  |  | 9126.2237
| Rate per Each |  |  |  | 9126.2237
| Say |  |  |  | 9126
9126
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.6 | 32 amps TPN, 4 way |  |  | DSR Rate Rs. | 18660
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1516 | 32 amps. TPN, 4 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 15960.76 | 15960.76
| Total cost of materials |  |  |  | 15960.76
| Cartage @ 1 % of A1 |  |  |  | 159.6076
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 16226.3176
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2433.95
| TOTAL |  |  |  | 18660.2676
| Rate per Each |  |  |  | 18660.2676
| Say |  |  |  | 18660
18660
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.7 | 32 amps TPN, 6 way |  |  | DSR Rate Rs. | 24505
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1517 | 32 amps. TPN, 6 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 20976.99 | 20976.99
| Total cost of materials |  |  |  | 20976.99
| Cartage @ 1 % of A1 |  |  |  | 209.7699
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 21309.0099
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3196.35
| TOTAL |  |  |  | 24505.3599
| Rate per Each |  |  |  | 24505.3599
| Say |  |  |  | 24505
24505
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.8 | 32 amps TPN, 8 way |  |  | DSR Rate Rs. | 34058
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1518 | 32 amps. TPN, 8 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 29185.38 | 29185.38
| Total cost of materials |  |  |  | 29185.38
| Cartage @ 1 % of A1 |  |  |  | 291.8538
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 29615.7838
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4442.37
| TOTAL |  |  |  | 34058.1538
| Rate per Each |  |  |  | 34058.1538
| Say |  |  |  | 34058
34058
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.9 | 63 amps TPN, 2 way |  |  | DSR Rate Rs. | 10397
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1519 | 63 amps. TPN, 2 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 8846.82 | 8846.82
| Total cost of materials |  |  |  | 8846.82
| Cartage @ 1 % of A1 |  |  |  | 88.4682
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 9041.2382
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1356.19
| TOTAL |  |  |  | 10397.4282
| Rate per Each |  |  |  | 10397.4282
| Say |  |  |  | 10397
10397
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.10 | 63 amps TPN, 4 way |  |  | DSR Rate Rs. | 17601
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1520 | 63 amps. TPN, 4 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 15048.72 | 15048.72
| Total cost of materials |  |  |  | 15048.72
| Cartage @ 1 % of A1 |  |  |  | 150.4872
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 15305.1572
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2295.77
| TOTAL |  |  |  | 17600.9272
| Rate per Each |  |  |  | 17600.9272
| Say |  |  |  | 17601
17601
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.11 | 63 amps TPN, 6 way |  |  | DSR Rate Rs. | 18997
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1521 | 63 amps. TPN, 6 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 16234.37 | 16234.37
| Total cost of materials |  |  |  | 16234.37
| Cartage @ 1 % of A1 |  |  |  | 162.3437
LABOUR
1001 | Wireman | day | 0.15 | 447 | 67.05
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 16518.9637
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2477.84
| TOTAL |  |  |  | 18996.8037
| Rate per Each |  |  |  | 18996.8037
| Say |  |  |  | 18997
18997
Analysis of rate
3.3 | Supplying, installing, testing and commissioning of following capacity TPN distribution tap off box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing rising mains complete with HRC fuses, interconnections, earthing etc. as required.
3.3.12 | 63 amps TPN, 8 way |  |  | DSR Rate Rs. | 32681
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1522 | 63 amps. TPN, 8 way, distribution tap off box with ISI marked HRC fuses for rising mains | each | 1 | 28000 | 28000
| Total cost of materials |  |  |  | 28000
| Cartage @ 1 % of A1 |  |  |  | 280
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 28418.55
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4262.78
| TOTAL |  |  |  | 32681.33
| Rate per Each |  |  |  | 32681.33
| Say |  |  |  | 32681
32681
Analysis of rate
3.4 | Supplying, installing, testing and commissioning of following capacity End Feed Unit made of 1.6mm thick sheet steel enclosure duly painted with powder coating to existing rising mains complete with TPN disconnector FSU and HRC fuses, mounting stands, cable end box, brass compression gland, connections, earthing etc. as required.
3.4.1 | 200 amps TPN |  |  | DSR Rate Rs. | 14871
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1526 | 200 amps. TPN, adaptor box with cable end box, with TPN disconnector FSU, ISI marked HRC fuses and brass compression gland for rising mains | each | 1 | 12586.19 | 12586.19
2211 | Aluminium lugs for 185 sq. mm cable | each | 3 | 23.27 | 69.81
2208 | Aluminium lugs for 95 sq. mm cable | each | 1 | 10.27 | 10.27
| Total cost of materials |  |  |  | 12666.27
| Cartage @ 1 % of A1 |  |  |  | 126.6627
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 12931.4827
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1939.72
| TOTAL |  |  |  | 14871.2027
| Rate per Each |  |  |  | 14871.2027
| Say |  |  |  | 14871
14871
Analysis of rate
3.4 | Supplying, installing, testing and commissioning of following capacity End Feed Unit made of 1.6mm thick sheet steel enclosure duly painted with powder coating to existing rising mains complete with TPN disconnector FSU and HRC fuses, mounting stands, cable end box, brass compression gland, connections, earthing etc. as required.
3.4.2 | 300 amps TPN |  |  | DSR Rate Rs. | 16341
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1527 | 300 amps. TPN, adaptor box with cable end box, with TPN disconnector FSU, ISI marked HRC fuses and brass compression gland for rising mains | each | 1 | 13680.65 | 13680.65
2214 | Aluminium lugs for 300 sq. mm cable | each | 3 | 55.83 | 167.49
2210 | Aluminium lugs for 150 sq. mm cable | each | 1 | 18.61 | 18.61
| Total cost of materials |  |  |  | 13866.75
| Cartage @ 1 % of A1 |  |  |  | 138.6675
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 14209.1675
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2131.38
| TOTAL |  |  |  | 16340.5475
| Rate per Each |  |  |  | 16340.5475
| Say |  |  |  | 16341
16341
Analysis of rate
3.4 | Supplying, installing, testing and commissioning of following capacity End Feed Unit made of 1.6mm thick sheet steel enclosure duly painted with powder coating to existing rising mains complete with TPN disconnector FSU and HRC fuses, mounting stands, cable end box, brass compression gland, connections, earthing etc. as required.
3.4.3 | 400 amps TPN |  |  | DSR Rate Rs. | 18107
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1528 | 400 amps. TPN, adaptor box with cable end box, with TPN disconnector FSU, ISI marked HRC fuses and brass compression gland for rising mains | each | 1 | 15048.72 | 15048.72
2215 | Aluminium lugs for 400 sq. mm cable | each | 3 | 80.68 | 242.04
2212 | Aluminium lugs for 225 sq. mm cable | each | 1 | 32.55 | 32.55
| Total cost of materials |  |  |  | 15323.31
| Cartage @ 1 % of A1 |  |  |  | 153.2331
LABOUR
1001 | Wireman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 15745.4931
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2361.82
| TOTAL |  |  |  | 18107.3131
| Rate per Each |  |  |  | 18107.3131
| Say |  |  |  | 18107
18107
Analysis of rate
3.4 | Supplying, installing, testing and commissioning of following capacity End Feed Unit made of 1.6mm thick sheet steel enclosure duly painted with powder coating to existing rising mains complete with TPN disconnector FSU and HRC fuses, mounting stands, cable end box, brass compression gland, connections, earthing etc. as required.
3.4.4 | 600 amps TPN |  |  | DSR Rate Rs. | 19598
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1529 | 600 amps. TPN, adaptor box with cable end box, with TPN disconnector FSU, ISI marked HRC fuses and brass compression gland for rising mains | each | 1 | 16234.37 | 16234.37
2214 | Aluminium lugs for 300 sq. mm cable | each | 6 | 55.83 | 334.98
2210 | Aluminium lugs for 150 sq. mm cable | each | 2 | 18.61 | 37.22
| Total cost of materials |  |  |  | 16606.57
| Cartage @ 1 % of A1 |  |  |  | 166.0657
LABOUR
1001 | Wireman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 17041.5857
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2556.24
| TOTAL |  |  |  | 19597.8257
| Rate per Each |  |  |  | 19597.8257
| Say |  |  |  | 19598
19598
Analysis of rate
3.4 | Supplying, installing, testing and commissioning of following capacity End Feed Unit made of 1.6mm thick sheet steel enclosure duly painted with powder coating to existing rising mains complete with TPN disconnector FSU and HRC fuses, mounting stands, cable end box, brass compression gland, connections, earthing etc. as required.
3.4.5 | 800 amps TPN |  |  | DSR Rate Rs. | 22081
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1530 | 800 amps. TPN, adaptor box with cable end box, with TPN disconnector FSU, ISI marked HRC fuses and brass compression gland for rising mains | each | 1 | 18058.46 | 18058.46
2215 | Aluminium lugs for 400 sq. mm cable | each | 6 | 80.68 | 484.08
2212 | Aluminium lugs for 225 sq. mm cable | each | 2 | 32.55 | 65.1
| Total cost of materials |  |  |  | 18607.64
| Cartage @ 1 % of A1 |  |  |  | 186.0764
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 19201.2164
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2880.18
| TOTAL |  |  |  | 22081.3964
| Rate per Each |  |  |  | 22081.3964
| Say |  |  |  | 22081
22081
Analysis of rate
3.5 | Supplying, installation, including suspension, testing and commissioning of following capacity bus trunking with aluminium bus bars in 1.6mm thick sheet steel enclosure in convenient sections for use on, 3 phase, 4 wire, 415 volts, 50 Hz, A.C. supply including jointing of sections, flexible joints, expansion joints, bends and earthing with 2 runs of galvanised iron strips, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.5.1 | 800 amps |  |  | DSR Rate Rs. | 8482
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1531 | 800 amps. TPN, bus trunking with aluminium busbars | metre | 10 | 7068.34 | 70683.4
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 8.82 | 37.8 | 333.4
2801 | MS Suspender 6 mm dia 0.75m long | each | 14 | 21 | 294
2856 | Steel fastener 8 mm X 75 mm | each | 14 | 7 | 98
| Total cost of materials |  |  |  | 71408.8
| Cartage @ 1 % of A1 |  |  |  | 714.088
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 73752.888
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11062.93
| Cost for 10 Metre |  |  |  | 84815.818
| Rate per Metre |  |  |  | 8481.5818
| Say |  |  |  | 8482
8482
Analysis of rate
3.5 | Supplying, installation, including suspension, testing and commissioning of following capacity bus trunking with aluminium bus bars in 1.6mm thick sheet steel enclosure in convenient sections for use on, 3 phase, 4 wire, 415 volts, 50 Hz, A.C. supply including jointing of sections, flexible joints, expansion joints, bends and earthing with 2 runs of galvanised iron strips, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.5.2 | 1000 amps |  |  | DSR Rate Rs. | 10018
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1532 | 1000 amps. TPN, bus trunking with aluminium busbars | metre | 10 | 8390.8 | 83908
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 8.82 | 37.8 | 333.4
2801 | MS Suspender 6 mm dia 0.75m long | each | 14 | 21 | 294
2856 | Steel fastener 8 mm X 75 mm | each | 14 | 7 | 98
| Total cost of materials |  |  |  | 84633.4
| Cartage @ 1 % of A1 |  |  |  | 846.334
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 87109.734
| OVERHEADS & PROFIT @ 15 % |  |  |  | 13066.46
| Cost for 10 Metre |  |  |  | 100176.194
| Rate per Metre |  |  |  | 10017.6194
| Say |  |  |  | 10018
10018
Analysis of rate
3.5 | Supplying, installation, including suspension, testing and commissioning of following capacity bus trunking with aluminium bus bars in 1.6mm thick sheet steel enclosure in convenient sections for use on, 3 phase, 4 wire, 415 volts, 50 Hz, A.C. supply including jointing of sections, flexible joints, expansion joints, bends and earthing with 2 runs of galvanised iron strips, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.5.3 | 1250 amps |  |  | DSR Rate Rs. | 12875
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1533 | 1250 amps. TPN, bus trunking with aluminium busbars | metre | 10 | 10762.11 | 107621.1
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 11.03 | 37.8 | 416.93
2801 | MS Suspender 6 mm dia 0.75m long | each | 14 | 21 | 294
2856 | Steel fastener 8 mm X 75 mm | each | 14 | 7 | 98
| Total cost of materials |  |  |  | 108430.03
| Cartage @ 1 % of A1 |  |  |  | 1084.3003
LABOUR
1001 | Wireman | day | 3 | 447 | 1341
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 111959.3303
| OVERHEADS & PROFIT @ 15 % |  |  |  | 16793.9
| Cost for 10 Metre |  |  |  | 128753.2303
| Rate per Metre |  |  |  | 12875.323
| Say |  |  |  | 12875
12875
Analysis of rate
3.5 | Supplying, installation, including suspension, testing and commissioning of following capacity bus trunking with aluminium bus bars in 1.6mm thick sheet steel enclosure in convenient sections for use on, 3 phase, 4 wire, 415 volts, 50 Hz, A.C. supply including jointing of sections, flexible joints, expansion joints, bends and earthing with 2 runs of galvanised iron strips, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.5.4 | 1400 amps |  |  | DSR Rate Rs. | 16053
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1534 | 1400 amps. TPN, bus trunking with aluminium busbars | metre | 10 | 13498.24 | 134982.4
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 11.03 | 37.8 | 416.93
2801 | MS Suspender 6 mm dia 0.75m long | each | 14 | 21 | 294
2856 | Steel fastener 8 mm X 75 mm | each | 14 | 7 | 98
| Total cost of materials |  |  |  | 135791.33
| Cartage @ 1 % of A1 |  |  |  | 1357.9133
LABOUR
1001 | Wireman | day | 3 | 447 | 1341
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 139594.2433
| OVERHEADS & PROFIT @ 15 % |  |  |  | 20939.14
| Cost for 10 Metre |  |  |  | 160533.3833
| Rate per Metre |  |  |  | 16053.3383
| Say |  |  |  | 16053
16053
Analysis of rate
3.5 | Supplying, installation, including suspension, testing and commissioning of following capacity bus trunking with aluminium bus bars in 1.6mm thick sheet steel enclosure in convenient sections for use on, 3 phase, 4 wire, 415 volts, 50 Hz, A.C. supply including jointing of sections, flexible joints, expansion joints, bends and earthing with 2 runs of galvanised iron strips, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.5.4 | 1400 amps |  |  | DSR Rate Rs. | 16095
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1535 | 1600 amps. TPN, bus trunking with aluminium busbars | metre | 10 | 13498.24 | 134982.4
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 9.8 | 37.8 | 370.44
2801 | MS Suspender 6 mm dia 0.75m long | each | 14 | 21 | 294
2856 | Steel fastener 8 mm X 75 mm | each | 14 | 7 | 98
| Total cost of materials |  |  |  | 135744.84
| Cartage @ 1 % of A1 |  |  |  | 1357.4484
LABOUR
1001 | Wireman | day | 3.5 | 447 | 1564.5
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 139954.7884
| OVERHEADS & PROFIT @ 15 % |  |  |  | 20993.22
| Cost for 10 Metre |  |  |  | 160948.0084
| Rate per Metre |  |  |  | 16094.8008
| Say |  |  |  | 16095
16095
Analysis of rate
3.6 | Supplying, installation, testing and commissioning of following capacity overhead distribution bus trunking with aluminium bus bars in 1.6mm thick sheet steel enclosure in convenient sections with provision of tapping points for use on, 3 phase, 4 wire, 415 volts, 50 Hz, A.C. supply including jointing of sections, bends, earthing with 2 runs of galvanised iron strips, all installation accessories etc. as required.
3.6.1 | 200 amps |  |  | DSR Rate Rs. | 4933
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1536 | 200 amps. TPN, overhead busbars with aluminium busbars | metre | 10 | 4013 | 40130
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 8.82 | 37.8 | 333.4
2801 | MS Suspender 6 mm dia 0.75m long | each | 14 | 21 | 294
2856 | Steel fastener 8 mm X 75 mm | each | 14 | 7 | 98
| Total cost of materials |  |  |  | 40855.4
| Cartage @ 1 % of A1 |  |  |  | 408.554
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 42893.954
| OVERHEADS & PROFIT @ 15 % |  |  |  | 6434.09
| Cost for 10 Metre |  |  |  | 49328.044
| Rate per Metre |  |  |  | 4932.8044
| Say |  |  |  | 4933
4933
Analysis of rate
3.6 | Supplying, installation, testing and commissioning of following capacity overhead distribution bus trunking with aluminium bus bars in 1.6mm thick sheet steel enclosure in convenient sections with provision of tapping points for use on, 3 phase, 4 wire, 415 volts, 50 Hz, A.C. supply including jointing of sections, bends, earthing with 2 runs of galvanised iron strips, all installation accessories etc. as required.
3.6.2 | 400 amps |  |  | DSR Rate Rs. | 6310
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1537 | 400 amps. TPN, overhead busbars with aluminium busbars | metre | 10 | 5198.64 | 51986.4
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 8.82 | 37.8 | 333.4
2801 | MS Suspender 6 mm dia 0.75m long | each | 14 | 21 | 294
2856 | Steel fastener 8 mm X 75 mm | each | 14 | 7 | 98
| Total cost of materials |  |  |  | 52711.8
| Cartage @ 1 % of A1 |  |  |  | 527.118
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 54868.918
| OVERHEADS & PROFIT @ 15 % |  |  |  | 8230.34
| Cost for 10 Metre |  |  |  | 63099.258
| Rate per Metre |  |  |  | 6309.9258
| Say |  |  |  | 6310
6310
Analysis of rate
3.7 | Supplying, installing, testing and commissioning of following capacity TPN tap off box / plug-in box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing overhead bus bar system complete with TPN disconnector FSU and HRC fuses, connections, earthing etc. as required.
3.7.1 | 32 amps |  |  | DSR Rate Rs. | 5360
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1538 | 32 amps. TPN, plug-in-box with TPN disconnector FSU and ISI marked HRC fuses for overhead busbars | each | 1 | 4534.16 | 4534.16
| Total cost of materials |  |  |  | 4534.16
| Cartage @ 1 % of A1 |  |  |  | 45.3416
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 4661.0016
| OVERHEADS & PROFIT @ 15 % |  |  |  | 699.15
| TOTAL |  |  |  | 5360.1516
| Rate per Each |  |  |  | 5360.1516
| Say |  |  |  | 5360
5360
Analysis of rate
3.7 | Supplying, installing, testing and commissioning of following capacity TPN tap off box / plug-in box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing overhead bus bar system complete with TPN disconnector FSU and HRC fuses, connections, earthing etc. as required.
3.7.2 | 63 amps |  |  | DSR Rate Rs. | 6024
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1539 | 63 amps. TPN, plug-in-box with TPN disconnector FSU and ISI marked HRC fuses for overhead busbars | each | 1 | 5081.38 | 5081.38
| Total cost of materials |  |  |  | 5081.38
| Cartage @ 1 % of A1 |  |  |  | 50.8138
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 5238.1438
| OVERHEADS & PROFIT @ 15 % |  |  |  | 785.72
| TOTAL |  |  |  | 6023.8638
| Rate per Each |  |  |  | 6023.8638
| Say |  |  |  | 6024
6024
Analysis of rate
3.7 | Supplying, installing, testing and commissioning of following capacity TPN tap off box / plug-in box made of 1.6mm thick sheet steel enclosure duly painted with powder coating on existing overhead bus bar system complete with TPN disconnector FSU and HRC fuses, connections, earthing etc. as required.
3.7.3 | 63 amps |  |  | DSR Rate Rs. | 6932
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1540 | 100 amps. TPN, plug-in-box with TPN disconnector FSU and ISI marked HRC fuses for overhead busbars | each | 1 | 5863.14 | 5863.14
| Total cost of materials |  |  |  | 5863.14
| Cartage @ 1 % of A1 |  |  |  | 58.6314
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 6027.7214
| OVERHEADS & PROFIT @ 15 % |  |  |  | 904.16
| TOTAL |  |  |  | 6931.8814
| Rate per Each |  |  |  | 6931.8814
| Say |  |  |  | 6932
6932
Analysis of rate
3.8 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Rising Mains for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.8.1 | 200 amps 15KA SC for 1 sec |  |  | DSR Rate Rs. | 5382
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1551 | 200 amps. TPN, compact type rising mains with aluminium busbar including all accessories | metre | 10 | 4407.53 | 44075.3
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 44148.63
| Cartage @ 1 % of A1 |  |  |  | 441.4863
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 46801.3663
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7020.2
| Cost for 10 Metre |  |  |  | 53821.5663
| Rate per Metre |  |  |  | 5382.1566
| Say |  |  |  | 5382
5382
Analysis of rate
3.8 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Rising Mains for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.8.2 | 315 amps 25KA SC for 1 sec |  |  | DSR Rate Rs. | 5806
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1552 | 315 amps. TPN, compact type rising mains with aluminium busbar including all accessories | metre | 10 | 4772.54 | 47725.4
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 47798.73
| Cartage @ 1 % of A1 |  |  |  | 477.9873
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 50487.9673
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7573.2
| Cost for 10 Metre |  |  |  | 58061.1673
| Rate per Metre |  |  |  | 5806.1167
| Say |  |  |  | 5806
5806
Analysis of rate
3.8 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Rising Mains for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.8.3 | 400 amps 30KA SC for 1 sec |  |  | DSR Rate Rs. | 6446
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1553 | 400 amps. TPN, compact type rising mains with aluminium busbar including all accessories | metre | 10 | 5304.11 | 53041.1
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 53114.43
| Cartage @ 1 % of A1 |  |  |  | 531.1443
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 56050.5743
| OVERHEADS & PROFIT @ 15 % |  |  |  | 8407.59
| Cost for 10 Metre |  |  |  | 64458.1643
| Rate per Metre |  |  |  | 6445.8164
| Say |  |  |  | 6446
6446
Analysis of rate
3.8 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Rising Mains for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.8.4 | 500 amps 30KA SC for 1 sec |  |  | DSR Rate Rs. | 7401
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1554 | 500 amps. TPN, compact type rising mains with aluminium busbar including all accessories | metre | 10 | 6105.88 | 61058.8
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 61132.13
| Cartage @ 1 % of A1 |  |  |  | 611.3213
LABOUR
1001 | Wireman | day | 2.25 | 447 | 1005.75
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 64352.2013
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9652.83
| Cost for 10 Metre |  |  |  | 74005.0313
| Rate per Metre |  |  |  | 7400.5031
| Say |  |  |  | 7401
7401
Analysis of rate
3.8 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Rising Mains for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.8.5 | 630 amps 30KA SC for 1 sec |  |  | DSR Rate Rs. | 8814
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1555 | 630 amps. TPN, compact type rising mains with aluminium busbar including all accessories | metre | 10 | 7302.78 | 73027.8
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 73101.13
| Cartage @ 1 % of A1 |  |  |  | 731.0113
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 76644.6413
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11496.7
| Cost for 10 Metre |  |  |  | 88141.3413
| Rate per Metre |  |  |  | 8814.1341
| Say |  |  |  | 8814
8814
Analysis of rate
3.8 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Rising Mains for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.8.6 | 630 amps 30KA SC for 1 sec |  |  | DSR Rate Rs. | 12104
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1556 | 800 amps. TPN, compact type rising mains with aluminium busbar including all accessories | metre | 10 | 10135.13 | 101351.3
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 101424.63
| Cartage @ 1 % of A1 |  |  |  | 1014.2463
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 105251.3763
| OVERHEADS & PROFIT @ 15 % |  |  |  | 15787.71
| Cost for 10 Metre |  |  |  | 121039.0863
| Rate per Metre |  |  |  | 12103.9086
| Say |  |  |  | 12104
12104
Analysis of rate
3.8 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Rising Mains for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.8.7 | 1000 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 14003
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1557 | 1000 amps. TPN, compact type rising mains with aluminium busbar including all accessories | metre | 10 | 11770.31 | 117703.1
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 117776.43
| Cartage @ 1 % of A1 |  |  |  | 1177.7643
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 121766.6943
| OVERHEADS & PROFIT @ 15 % |  |  |  | 18265
| Cost for 10 Metre |  |  |  | 140031.6943
| Rate per Metre |  |  |  | 14003.1694
| Say |  |  |  | 14003
14003
Analysis of rate
3.8 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Rising Mains for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.8.8 | 1250 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 16634
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1558 | 1250 amps. TPN, compact type rising mains with aluminium busbar including all accessories | metre | 10 | 14035.01 | 140350.1
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 140423.43
| Cartage @ 1 % of A1 |  |  |  | 1404.2343
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 144640.1643
| OVERHEADS & PROFIT @ 15 % |  |  |  | 21696.02
| Cost for 10 Metre |  |  |  | 166336.1843
| Rate per Metre |  |  |  | 16633.6184
| Say |  |  |  | 16634
16634
Analysis of rate
3.9 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.9.1 | 200 amps 15KA SC for 1 sec |  |  | DSR Rate Rs. | 5467
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1559 | 200 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 4480.31 | 44803.1
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 44876.43
| Cartage @ 1 % of A1 |  |  |  | 448.7643
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 47536.4443
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7130.47
| Cost for 10 Metre |  |  |  | 54666.9143
| Rate per Metre |  |  |  | 5466.6914
| Say |  |  |  | 5467
5467
Analysis of rate
3.9 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.9.2 | 315 amps 25KA SC for 1 sec |  |  | DSR Rate Rs. | 5819
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1560 | 315 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 4784.06 | 47840.6
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 47913.93
| Cartage @ 1 % of A1 |  |  |  | 479.1393
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 50604.3193
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7590.65
| Cost for 10 Metre |  |  |  | 58194.9693
| Rate per Metre |  |  |  | 5819.4969
| Say |  |  |  | 5819
5819
Analysis of rate
3.9 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.9.3 | 400 amps 30KA SC for 1 sec |  |  | DSR Rate Rs. | 6459
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1561 | 400 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 5315.63 | 53156.3
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 53229.63
| Cartage @ 1 % of A1 |  |  |  | 532.2963
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 56166.9263
| OVERHEADS & PROFIT @ 15 % |  |  |  | 8425.04
| Cost for 10 Metre |  |  |  | 64591.9663
| Rate per Metre |  |  |  | 6459.1966
| Say |  |  |  | 6459
6459
Analysis of rate
3.9 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.9.4 | 500 amps 35KA SC for 1 sec |  |  | DSR Rate Rs. | 7453
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1562 | 500 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 6150.94 | 61509.4
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 61582.73
| Cartage @ 1 % of A1 |  |  |  | 615.8273
LABOUR
1001 | Wireman | day | 2.25 | 447 | 1005.75
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 64807.3073
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9721.1
| Cost for 10 Metre |  |  |  | 74528.4073
| Rate per Metre |  |  |  | 7452.8407
| Say |  |  |  | 7453
7453
Analysis of rate
3.9 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.9.5 | 630 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 8799
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1563 | 630 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 7290 | 72900
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 72973.33
| Cartage @ 1 % of A1 |  |  |  | 729.7333
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 76515.5633
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11477.33
| Cost for 10 Metre |  |  |  | 87992.8933
| Rate per Metre |  |  |  | 8799.2893
| Say |  |  |  | 8799
8799
Analysis of rate
3.9 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.9.6 | 800 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 11357
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1564 | 800 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 9492.19 | 94921.9
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 94995.23
| Cartage @ 1 % of A1 |  |  |  | 949.9523
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 98757.6823
| OVERHEADS & PROFIT @ 15 % |  |  |  | 14813.65
| Cost for 10 Metre |  |  |  | 113571.3323
| Rate per Metre |  |  |  | 11357.1332
| Say |  |  |  | 11357
11357
Analysis of rate
3.9 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.9.7 | 1000 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 13121
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1565 | 1000 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 11010.94 | 110109.4
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 110182.73
| Cartage @ 1 % of A1 |  |  |  | 1101.8273
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 114097.0573
| OVERHEADS & PROFIT @ 15 % |  |  |  | 17114.56
| Cost for 10 Metre |  |  |  | 131211.6173
| Rate per Metre |  |  |  | 13121.1617
| Say |  |  |  | 13121
13121
Analysis of rate
3.9 | Supplying, installing on wall, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.9.8 | 1250 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 15326
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1566 | 1250 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 12909.38 | 129093.8
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
| Total cost of materials |  |  |  | 129167.13
| Cartage @ 1 % of A1 |  |  |  | 1291.6713
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 133271.3013
| OVERHEADS & PROFIT @ 15 % |  |  |  | 19990.7
| Cost for 10 Metre |  |  |  | 153262.0013
| Rate per Metre |  |  |  | 15326.2001
| Say |  |  |  | 15326
15326
Analysis of rate
3.10 | Supplying, installing suspension on ceiling, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.10.1 | 200 amps 15KA SC for 1 sec |  |  | DSR Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1559 | 200 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 4480.31 | 44803.1
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2801 | MS Suspender 6 mm dia 0.75m long | each | 14 | 21 | 294
| Total cost of materials |  |  |  | 45170.43
| Cartage @ 1 % of A1 |  |  |  | 451.7043
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 47833.3843
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7175.01
| Cost for 10 Metre |  |  |  | 55008.3943
| Rate per Metre |  |  |  | 5500.8394
| Say |  |  |  | 5501
5501
Analysis of rate
3.10 | Supplying, installing suspension on ceiling, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.10.2 | 315 amps 25KA SC for 1 sec |  |  | DSR Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1560 | 315 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 4784.06 | 47840.6
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2801 | MS Suspender 6 mm dia 0.75m long | each | 14 | 21 | 294
| Total cost of materials |  |  |  | 48207.93
| Cartage @ 1 % of A1 |  |  |  | 482.0793
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 50901.2593
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7635.19
| Cost for 10 Metre |  |  |  | 58536.4493
| Rate per Metre |  |  |  | 5853.6449
| Say |  |  |  | 5854
5854
Analysis of rate
3.10 | Supplying, installing suspension on ceiling, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.10.3 | 400 amps 30KA SC for 1 sec |  |  | DSR Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1561 | 400 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 5315.63 | 53156.3
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2801 | MS Suspender 6 mm dia 0.75m long | each | 14 | 21 | 294
| Total cost of materials |  |  |  | 53523.63
| Cartage @ 1 % of A1 |  |  |  | 535.2363
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 56463.8663
| OVERHEADS & PROFIT @ 15 % |  |  |  | 8469.58
| Cost for 10 Metre |  |  |  | 64933.4463
| Rate per Metre |  |  |  | 6493.3446
| Say |  |  |  | 6493
6493
Analysis of rate
3.10 | Supplying, installing suspension on ceiling, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.10.4 | 500 amps 35KA SC for 1 sec |  |  | DSR Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1562 | 500 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 6150.94 | 61509.4
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 61940.01
| Cartage @ 1 % of A1 |  |  |  | 619.4001
LABOUR
1001 | Wireman | day | 2.25 | 447 | 1005.75
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.25 | 368 | 1196
| TOTAL |  |  |  | 65168.1601
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9775.22
| Cost for 10 Metre |  |  |  | 74943.3801
| Rate per Metre |  |  |  | 7494.338
| Say |  |  |  | 7494
7494
Analysis of rate
3.10 | Supplying, installing suspension on ceiling, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.10.5 | 630 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1563 | 630 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 7290 | 72900
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 73330.61
| Cartage @ 1 % of A1 |  |  |  | 733.3061
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 76876.4161
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11531.46
| Cost for 10 Metre |  |  |  | 88407.8761
| Rate per Metre |  |  |  | 8840.7876
| Say |  |  |  | 8841
8841
Analysis of rate
3.10 | Supplying, installing suspension on ceiling, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.10.6 | 800 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1564 | 800 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 9492.19 | 94921.9
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 95352.51
| Cartage @ 1 % of A1 |  |  |  | 953.5251
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 99118.5351
| OVERHEADS & PROFIT @ 15 % |  |  |  | 14867.78
| Cost for 10 Metre |  |  |  | 113986.3151
| Rate per Metre |  |  |  | 11398.6315
| Say |  |  |  | 11399
11399
Analysis of rate
3.10 | Supplying, installing suspension on ceiling, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.10.7 | 1000 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1565 | 1000 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 11010.94 | 110109.4
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2803 | MS Suspender 10 mm dia 0.75m long | each | 14 | 35.91 | 502.74
| Total cost of materials |  |  |  | 110685.47
| Cartage @ 1 % of A1 |  |  |  | 1106.8547
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 114604.8247
| OVERHEADS & PROFIT @ 15 % |  |  |  | 17190.72
| Cost for 10 Metre |  |  |  | 131795.5447
| Rate per Metre |  |  |  | 13179.5545
| Say |  |  |  | 13180
13180
Analysis of rate
3.10 | Supplying, installing suspension on ceiling, testing and commissioning of following capacity Air Insulated Compact Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints, fire barrier at each floor, provision of tapping at every metre, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.10.8 | 1250 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1566 | 1250 amps. TPN, compact type bus trunking with aluminium busbar including elbows and other all accessories | metre | 10 | 12909.38 | 129093.8
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2803 | MS Suspender 10 mm dia 0.75m long | each | 14 | 35.91 | 502.74
| Total cost of materials |  |  |  | 129669.87
| Cartage @ 1 % of A1 |  |  |  | 1296.6987
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 133779.0687
| OVERHEADS & PROFIT @ 15 % |  |  |  | 20066.86
| Cost for 10 Metre |  |  |  | 153845.9287
| Rate per Metre |  |  |  | 15384.5929
| Say |  |  |  | 15385
15385
Analysis of rate
3.11 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity End Feed Unit for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply made with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB/ACB (but without MCCB/ACB) complete with necessary joints including clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.11.1 | 200 amps 15KA SC for 1 sec |  |  | DSR Rate Rs. | 4004
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1567 | 200 amps. TPN, End Feed Unit for compact rising mains including all accessories | each | 1 | 3366.56 | 3366.56
| Total cost of materials |  |  |  | 3366.56
| Cartage @ 1 % of A1 |  |  |  | 33.6656
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 3481.7256
| OVERHEADS & PROFIT @ 15 % |  |  |  | 522.26
| TOTAL |  |  |  | 4003.9856
| Rate per Each |  |  |  | 4003.9856
| Say |  |  |  | 4004
4004
Analysis of rate
3.11 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity End Feed Unit for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply made with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB/ACB (but without MCCB/ACB) complete with necessary joints including clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.11.2 | 315 amps 25KA SC for 1 sec |  |  | DSR Rate Rs. | 4169
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1568 | 315 amps. TPN, End Feed Unit for compact rising mains including all accessories | each | 1 | 3508.31 | 3508.31
| Total cost of materials |  |  |  | 3508.31
| Cartage @ 1 % of A1 |  |  |  | 35.0831
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 3624.8931
| OVERHEADS & PROFIT @ 15 % |  |  |  | 543.73
| TOTAL |  |  |  | 4168.6231
| Rate per Each |  |  |  | 4168.6231
| Say |  |  |  | 4169
4169
Analysis of rate
3.11 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity End Feed Unit for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply made with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB/ACB (but without MCCB/ACB) complete with necessary joints including clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.11.3 | 400 amps 30KA SC for 1 sec |  |  | DSR Rate Rs. | 5308
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1569 | 400 amps. TPN, End Feed Unit for compact rising mains including all accessories | each | 1 | 4465.13 | 4465.13
| Total cost of materials |  |  |  | 4465.13
| Cartage @ 1 % of A1 |  |  |  | 44.6513
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 4615.7313
| OVERHEADS & PROFIT @ 15 % |  |  |  | 692.36
| TOTAL |  |  |  | 5308.0913
| Rate per Each |  |  |  | 5308.0913
| Say |  |  |  | 5308
5308
Analysis of rate
3.11 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity End Feed Unit for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply made with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB/ACB (but without MCCB/ACB) complete with necessary joints including clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.11.4 | 500 amps 35KA SC for 1 sec |  |  | DSR Rate Rs. | 5555
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1570 | 500 amps. TPN, End Feed Unit for compact rising mains including all accessories | each | 1 | 4677.75 | 4677.75
| Total cost of materials |  |  |  | 4677.75
| Cartage @ 1 % of A1 |  |  |  | 46.7775
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 4830.4775
| OVERHEADS & PROFIT @ 15 % |  |  |  | 724.57
| TOTAL |  |  |  | 5555.0475
| Rate per Each |  |  |  | 5555.0475
| Say |  |  |  | 5555
5555
Analysis of rate
3.11 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity End Feed Unit for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply made with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB/ACB (but without MCCB/ACB) complete with necessary joints including clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.11.5 | 630 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 6786
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1571 | 630 amps. TPN, End Feed Unit for compact rising mains including all accessories | each | 1 | 5705.44 | 5705.44
| Total cost of materials |  |  |  | 5705.44
| Cartage @ 1 % of A1 |  |  |  | 57.0544
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 5901.0444
| OVERHEADS & PROFIT @ 15 % |  |  |  | 885.16
| TOTAL |  |  |  | 6786.2044
| Rate per Each |  |  |  | 6786.2044
| Say |  |  |  | 6786
6786
Analysis of rate
3.11 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity End Feed Unit for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply made with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB/ACB (but without MCCB/ACB) complete with necessary joints including clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.11.6 | 800 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 8009
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1572 | 800 amps. TPN, End Feed Unit for compact rising mains including all accessories | each | 1 | 6758.44 | 6758.44
| Total cost of materials |  |  |  | 6758.44
| Cartage @ 1 % of A1 |  |  |  | 67.5844
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 6964.5744
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1044.69
| TOTAL |  |  |  | 8009.2644
| Rate per Each |  |  |  | 8009.2644
| Say |  |  |  | 8009
8009
Analysis of rate
3.11 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity End Feed Unit for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply made with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB/ACB (but without MCCB/ACB) complete with necessary joints including clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.11.7 | 1000 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 8968
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1573 | 1000 amps. TPN, End Feed Unit for compact rising mains including all accessories | each | 1 | 7583.63 | 7583.63
| Total cost of materials |  |  |  | 7583.63
| Cartage @ 1 % of A1 |  |  |  | 75.8363
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 7798.0163
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1169.7
| TOTAL |  |  |  | 8967.7163
| Rate per Each |  |  |  | 8967.7163
| Say |  |  |  | 8968
8968
Analysis of rate
3.11 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity End Feed Unit for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply made with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB/ACB (but without MCCB/ACB) complete with necessary joints including clamping brackets, angle iron bracket, steel fasteners, connecting to earthing system etc. as required
3.11.8 | 1200 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 9462
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1574 | 1250 amps. TPN, End Feed Unit for compact rising mains including all accessories | each | 1 | 8008.88 | 8008.88
| Total cost of materials |  |  |  | 8008.88
| Cartage @ 1 % of A1 |  |  |  | 80.0888
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 8227.5188
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1234.13
| TOTAL |  |  |  | 9461.6488
| Rate per Each |  |  |  | 9461.6488
| Say |  |  |  | 9462
9462
Analysis of rate
3.12 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity Plug In/ Tap Off Box for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB (but without MCCB) complete etc. as required
3.12.1 | 125 amps 15KA SC for 1 sec |  |  | DSR Rate Rs. | 4621
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1575 | 125 amps. TPN, TAP OFF Box for compact rising mains including all accessories | each | 1 | 3898.13 | 3898.13
| Total cost of materials |  |  |  | 3898.13
| Cartage @ 1 % of A1 |  |  |  | 38.9813
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 4018.6113
| OVERHEADS & PROFIT @ 15 % |  |  |  | 602.79
| TOTAL |  |  |  | 4621.4013
| Rate per Each |  |  |  | 4621.4013
| Say |  |  |  | 4621
4621
Analysis of rate
3.12 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity Plug In/ Tap Off Box for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB (but without MCCB) complete etc. as required
3.12.2 | 200 amps 25KA SC for 1 sec |  |  | DSR Rate Rs. | 5856
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1576 | 200 amps. TPN, TAP OFF Box for compact rising mains including all accessories | each | 1 | 4961.25 | 4961.25
| Total cost of materials |  |  |  | 4961.25
| Cartage @ 1 % of A1 |  |  |  | 49.6125
LABOUR
1001 | Wireman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 5092.3625
| OVERHEADS & PROFIT @ 15 % |  |  |  | 763.85
| TOTAL |  |  |  | 5856.2125
| Rate per Each |  |  |  | 5856.2125
| Say |  |  |  | 5856
5856
Analysis of rate
3.12 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity Plug In/ Tap Off Box for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB (but without MCCB) complete etc. as required
3.12.3 | 250 amps 30KA SC for 1 sec |  |  | DSR Rate Rs. | 7531
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1577 | 315 amps. TPN, TAP OFF Box for compact rising mains including all accessories | each | 1 | 6378.75 | 6378.75
| Total cost of materials |  |  |  | 6378.75
| Cartage @ 1 % of A1 |  |  |  | 63.7875
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 6548.4875
| OVERHEADS & PROFIT @ 15 % |  |  |  | 982.27
| TOTAL |  |  |  | 7530.7575
| Rate per Each |  |  |  | 7530.7575
| Say |  |  |  | 7531
7531
Analysis of rate
3.12 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity Plug In/ Tap Off Box for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB (but without MCCB) complete etc. as required
3.12.4 | 400 amps 35KA SC for 1 sec |  |  | DSR Rate Rs. | 7531
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1578 | 400 amps. TPN, TAP OFF Box for compact rising mains including all accessories | each | 1 | 6378.75 | 6378.75
| Total cost of materials |  |  |  | 6378.75
| Cartage @ 1 % of A1 |  |  |  | 63.7875
LABOUR
1001 | Wireman | day | 0.13 | 447 | 58.11
1007 | Khallasi | day | 0.13 | 368 | 47.84
| TOTAL |  |  |  | 6548.4875
| OVERHEADS & PROFIT @ 15 % |  |  |  | 982.27
| TOTAL |  |  |  | 7530.7575
| Rate per Each |  |  |  | 7530.7575
| Say |  |  |  | 7531
7531
Analysis of rate
3.12 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity Plug In/ Tap Off Box for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB (but without MCCB) complete etc. as required
3.12.5 | 500 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 10861
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1579 | 500 amps. TPN, TAP OFF Box for compact rising mains including all accessories | each | 1 | 9213.75 | 9213.75
| Total cost of materials |  |  |  | 9213.75
| Cartage @ 1 % of A1 |  |  |  | 92.1375
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 9444.4375
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1416.67
| TOTAL |  |  |  | 10861.1075
| Rate per Each |  |  |  | 10861.1075
| Say |  |  |  | 10861
10861
Analysis of rate
3.12 | Supplying, installing, connecting to existing Air Insulated Compact Type bus trunking/ rising mains, testing and commissioning of following capacity Plug In/ Tap Off Box for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with 1.6mm thick steel sheet enclosure duly powder coated with provision of MCCB (but without MCCB) complete etc. as required
3.12.6 | 630 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 10860
Details of cost for one each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1580 | 630 amps. TPN, TAP OFF Box for compact rising mains including all accessories | each | 1 | 9213 | 9213
| Total cost of materials |  |  |  | 9213
| Cartage @ 1 % of A1 |  |  |  | 92.13
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
| TOTAL |  |  |  | 9443.68
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1416.55
| TOTAL |  |  |  | 10860.23
| Rate per Each |  |  |  | 10860.23
| Say |  |  |  | 10860
10860
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.1 | 400 amps 25KA SC for 1 sec |  |  | DSR Rate Rs. | 8708
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1581 | 400 amps 25KA SC for 1 sec | metre | 10 | 7176.09 | 71760.9
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 72191.51
| Cartage @ 1 % of A1 |  |  |  | 721.9151
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 75725.9251
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11358.89
| Cost for 10 Metre |  |  |  | 87084.8151
| Rate per Metre |  |  |  | 8708.4815
| Say |  |  |  | 8708
8708
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.2 | 500 amps 30KA SC for 1 sec |  |  | DSR Rate Rs. | 9304
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1582 | 500 amps 30KA SC for 1 sec | metre | 10 | 7688.67 | 76886.7
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 77317.31
| Cartage @ 1 % of A1 |  |  |  | 773.1731
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 80902.9831
| OVERHEADS & PROFIT @ 15 % |  |  |  | 12135.45
| Cost for 10 Metre |  |  |  | 93038.4331
| Rate per Metre |  |  |  | 9303.8433
| Say |  |  |  | 9304
9304
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.3 | 630 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 10032
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1583 | 630 amps 50KA SC for 1 sec | metre | 10 | 8315.16 | 83151.6
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 83582.21
| Cartage @ 1 % of A1 |  |  |  | 835.8221
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 87230.5321
| OVERHEADS & PROFIT @ 15 % |  |  |  | 13084.58
| Cost for 10 Metre |  |  |  | 100315.1121
| Rate per Metre |  |  |  | 10031.5112
| Say |  |  |  | 10032
10032
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.4 | 800 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 11288
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1584 | 800 amps 50KA SC for 1 sec | metre | 10 | 9397.27 | 93972.7
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 94403.31
| Cartage @ 1 % of A1 |  |  |  | 944.0331
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 98159.8431
| OVERHEADS & PROFIT @ 15 % |  |  |  | 14723.98
| Cost for 10 Metre |  |  |  | 112883.8231
| Rate per Metre |  |  |  | 11288.3823
| Say |  |  |  | 11288
11288
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.5 | 1000 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 12618
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1585 | 1000 amps 50KA SC for 1 sec | metre | 10 | 10542.4 | 105424
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 105854.61
| Cartage @ 1 % of A1 |  |  |  | 1058.5461
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 109725.6561
| OVERHEADS & PROFIT @ 15 % |  |  |  | 16458.85
| Cost for 10 Metre |  |  |  | 126184.5061
| Rate per Metre |  |  |  | 12618.4506
| Say |  |  |  | 12618
12618
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.6 | 1250 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 14067
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1586 | 1250 amps 50KA SC for 1 sec | metre | 10 | 11789.3 | 117893
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 118323.61
| Cartage @ 1 % of A1 |  |  |  | 1183.2361
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 122319.3461
| OVERHEADS & PROFIT @ 15 % |  |  |  | 18347.9
| Cost for 10 Metre |  |  |  | 140667.2461
| Rate per Metre |  |  |  | 14066.7246
| Say |  |  |  | 14067
14067
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.7 | 1600 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 17044
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1587 | 1600 amps 50KA SC for 1 sec | metre | 10 | 14352.19 | 143521.9
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 143952.51
| Cartage @ 1 % of A1 |  |  |  | 1439.5251
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 148204.5351
| OVERHEADS & PROFIT @ 15 % |  |  |  | 22230.68
| Cost for 10 Metre |  |  |  | 170435.2151
| Rate per Metre |  |  |  | 17043.5215
| Say |  |  |  | 17044
17044
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.8 | 2000 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 20219
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1588 | 2000 amps 50KA SC for 1 sec | metre | 10 | 17085.94 | 170859.4
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 171290.01
| Cartage @ 1 % of A1 |  |  |  | 1712.9001
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 175815.4101
| OVERHEADS & PROFIT @ 15 % |  |  |  | 26372.31
| Cost for 10 Metre |  |  |  | 202187.7201
| Rate per Metre |  |  |  | 20218.772
| Say |  |  |  | 20219
20219
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.9 | 2500 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 26000
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1589 | 2500 amps 50KA SC for 1 sec | metre | 10 | 22063.64 | 220636.4
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 221067.01
| Cartage @ 1 % of A1 |  |  |  | 2210.6701
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 226090.1801
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33913.53
| Cost for 10 Metre |  |  |  | 260003.7101
| Rate per Metre |  |  |  | 26000.371
| Say |  |  |  | 26000
26000
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.10 | 3200 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 28686
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1590 | 3200 amps 50KA SC for 1 sec | metre | 10 | 24375.94 | 243759.4
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 244190.01
| Cartage @ 1 % of A1 |  |  |  | 2441.9001
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 249444.4101
| OVERHEADS & PROFIT @ 15 % |  |  |  | 37416.66
| Cost for 10 Metre |  |  |  | 286861.0701
| Rate per Metre |  |  |  | 28686.107
| Say |  |  |  | 28686
28686
Analysis of rate
3.13 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars, necessary joints, elbow joints & expansion joints and bends, fire barrier at each floor, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size (one on each side) including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required.
3.13.11 | 4000 amps 50KA SC for 1 sec |  |  | DSR Rate Rs. | 49763
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1591 | 4000 amps 50KA SC for 1 sec | metre | 10 | 42522.34 | 425223.4
Sandwich Type Bus Trunking for use on 3 phase 4 wire 415 volts, 50Hz A.C. supply with metal clad enclosure made of 1.6mm thick steel sheet duly powder coated in convenient sections complete with 4 Nos aluminium bus bars
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 1.94 | 37.8 | 73.33
=7 X 0.25m =1.75 @1.11kg/m = 1.94kg
2802 | MS Suspender 8 mm dia 0.75m long | each | 14 | 25.52 | 357.28
| Total cost of materials |  |  |  | 425654.01
| Cartage @ 1 % of A1 |  |  |  | 4256.5401
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1007 | Khallasi | day | 3.5 | 368 | 1288
| TOTAL |  |  |  | 432723.0501
| OVERHEADS & PROFIT @ 15 % |  |  |  | 64908.46
| Cost for 10 Metre |  |  |  | 497631.5101
| Rate per Metre |  |  |  | 49763.151
| Say |  |  |  | 49763
49763
CHAPTER 4 – CABLE TRAYS (Analysis of rate based on DAR)
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.1 | 100 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 348
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2701 | MS perforated cable tray painted with powder coating 100 X 50 X 1.6 mm | metre | 31.5 | 140.63 | 4429.85
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2717 | MS perforated cable tray Connector 100 X 50 X 1.6 mm | each | 9 | 26.85 | 241.65
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 3.33 | 37.8 | 125.87
= 20 X 0.15m =3 @1.11kg/m = 3.33kg
2855 | Steel fastener 6 mm X 75 mm | each | 40 | 5 | 200
2801 | MS Suspender 6 mm dia 0.75m long | each | 40 | 21 | 840
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 5917.37
| Cartage @ 1 % of A1 |  |  |  | 59.1737
LABOUR
1005 | Fitter, Grade 2 | day | 2 | 407 | 814
1010 | Mason, Grade 2 | day | 2 | 407 | 814
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 9076.5437
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1361.48
| Cost for 30 Metre |  |  |  | 10438.0237
| Rate per Metre |  |  |  | 347.9341
| Say |  |  |  | 348
348
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.2 | 150 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 393
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2702 | MS perforated cable tray painted with powder coating 150 X 50 X 1.6 mm | metre | 31.5 | 174.38 | 5492.97
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2718 | MS perforated cable tray Connector 150 X 50 X 1.6 mm | each | 9 | 34.65 | 311.85
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 4.44 | 37.8 | 167.83
= 20 X 0.2m =4 @1.11kg/m = 4.44kg
2855 | Steel fastener 6 mm X 75 mm | each | 40 | 5 | 200
2801 | MS Suspender 6 mm dia 0.75m long | each | 40 | 21 | 840
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 7092.65
| Cartage @ 1 % of A1 |  |  |  | 70.9265
LABOUR
1005 | Fitter, Grade 2 | day | 2 | 407 | 814
1010 | Mason, Grade 2 | day | 2 | 407 | 814
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 10263.5765
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1539.54
| Cost for 30 Metre |  |  |  | 11803.1165
| Rate per Metre |  |  |  | 393.4372
| Say |  |  |  | 393
393
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.3 | 200 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 460
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2703 | MS perforated cable tray painted with powder coating 225 X 50 X 1.6 mm | metre | 31.5 | 227.25 | 7158.38
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2719 | MS perforated cable tray Connector 225 X 50 X 1.6 mm | each | 9 | 35.52 | 319.68
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 5.55 | 37.8 | 209.79
= 20 X 0.25m =5 @1.11kg/m = 5.55kg
2855 | Steel fastener 6 mm X 75 mm | each | 40 | 5 | 200
2801 | MS Suspender 6 mm dia 0.75m long | each | 40 | 21 | 840
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 8807.85
| Cartage @ 1 % of A1 |  |  |  | 88.0785
LABOUR
1005 | Fitter, Grade 2 | day | 2 | 407 | 814
1010 | Mason, Grade 2 | day | 2 | 407 | 814
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 11995.9285
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1799.39
| Cost for 30 Metre |  |  |  | 13795.3185
| Rate per Metre |  |  |  | 459.844
| Say |  |  |  | 460
460
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.4 | 300 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 526
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2704 | MS perforated cable tray painted with powder coating 300 X 50 X 1.6 mm | metre | 31.5 | 279 | 8788.5
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2720 | MS perforated cable tray Connector 300 X 50 X 1.6 mm | each | 9 | 35.52 | 319.68
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 7.77 | 37.8 | 293.71
= 20 X 0.35m =7 @1.11kg/m = 7.77kg
2855 | Steel fastener 6 mm X 75 mm | each | 40 | 5 | 200
2801 | MS Suspender 6 mm dia 0.75m long | each | 40 | 21 | 840
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 10521.89
| Cartage @ 1 % of A1 |  |  |  | 105.2189
LABOUR
1005 | Fitter, Grade 2 | day | 2 | 407 | 814
1010 | Mason, Grade 2 | day | 2 | 407 | 814
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 13727.1089
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2059.07
| Cost for 30 Metre |  |  |  | 15786.1789
| Rate per Metre |  |  |  | 526.206
| Say |  |  |  | 526
526
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.5 | 375 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 692
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2705 | MS perforated cable tray painted with powder coating 375 X 50 X 2 mm | metre | 31.5 | 401.63 | 12651.35
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2721 | MS perforated cable tray Connector 375 X 50 X 2 mm | each | 9 | 38.98 | 350.82
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 17.77 | 37.8 | 671.71
= 20 X 0.425m =8.5 @2.09kg/m = 17.77kg
2855 | Steel fastener 6 mm X 75 mm | each | 40 | 5 | 200
2801 | MS Suspender 6 mm dia 0.75m long | each | 40 | 21 | 840
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 14793.88
| Cartage @ 1 % of A1 |  |  |  | 147.9388
LABOUR
1005 | Fitter, Grade 2 | day | 2 | 407 | 814
1010 | Mason, Grade 2 | day | 2 | 407 | 814
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 18041.8188
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2706.27
| Cost for 30 Metre |  |  |  | 20748.0888
| Rate per Metre |  |  |  | 691.603
| Say |  |  |  | 692
692
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.6 | 450 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 782
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2706 | MS perforated cable tray painted with powder coating 450 X 50 X 2 mm | metre | 31.5 | 464.63 | 14635.85
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2722 | MS perforated cable tray Connector 450 X 50 X 2 mm | each | 9 | 45.91 | 413.19
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 20.9 | 37.8 | 790.02
= 20 X 0.5m =10 @2.09kg/m = 20.9kg
2855 | Steel fastener 6 mm X 75 mm | each | 40 | 5 | 200
2802 | MS Suspender 8 mm dia 0.75m long | each | 40 | 25.52 | 1020.8
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 17139.86
| Cartage @ 1 % of A1 |  |  |  | 171.3986
LABOUR
1005 | Fitter, Grade 2 | day | 2 | 407 | 814
1010 | Mason, Grade 2 | day | 2 | 407 | 814
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 20411.2586
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3061.69
| Cost for 30 Metre |  |  |  | 23472.9486
| Rate per Metre |  |  |  | 782.4316
| Say |  |  |  | 782
782
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.7 | 600 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 950
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2707 | MS perforated cable tray painted with powder coating 600 X 50 X 2 mm | metre | 31.5 | 590.63 | 18604.85
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2723 | MS perforated cable tray Connector 600 X 50 X 2 mm | each | 9 | 50.25 | 452.25
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 27.17 | 37.8 | 1027.03
= 20 X 0.65m =13 @2.09kg/m = 27.17kg
2856 | Steel fastener 8 mm X 75 mm | each | 40 | 7 | 280
2802 | MS Suspender 8 mm dia 0.75m long | each | 40 | 25.52 | 1020.8
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 21464.93
| Cartage @ 1 % of A1 |  |  |  | 214.6493
LABOUR
1005 | Fitter, Grade 2 | day | 2 | 407 | 814
1010 | Mason, Grade 2 | day | 2 | 407 | 814
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 24779.5793
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3716.94
| Cost for 30 Metre |  |  |  | 28496.5193
| Rate per Metre |  |  |  | 949.884
| Say |  |  |  | 950
950
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.8 | 300 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 629
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2708 | MS perforated cable tray painted with powder coating 300 X 62.5 X 2 mm | metre | 31.5 | 360 | 11340
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2724 | MS perforated cable tray Connector 300 X 62.5 X 2 mm | each | 9 | 38.98 | 350.82
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 7.77 | 37.8 | 293.71
= 20 X 0.35m =7 @1.11kg/m = 7.77kg
2856 | Steel fastener 8 mm X 75 mm | each | 40 | 7 | 280
2801 | MS Suspender 6 mm dia 0.75m long | each | 40 | 21 | 840
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 13184.53
| Cartage @ 1 % of A1 |  |  |  | 131.8453
LABOUR
1005 | Fitter, Grade 2 | day | 2 | 407 | 814
1010 | Mason, Grade 2 | day | 2 | 407 | 814
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 16416.3753
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2462.46
| Cost for 30 Metre |  |  |  | 18878.8353
| Rate per Metre |  |  |  | 629.2945
| Say |  |  |  | 629
629
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.9 | 375 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 722
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2709 | MS perforated cable tray painted with powder coating 375 X 62.5 X 2 mm | metre | 31.5 | 421.88 | 13289.22
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2725 | MS perforated cable tray Connector 375 X 62.5 X 2 mm | each | 9 | 45.05 | 405.45
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 17.77 | 37.8 | 671.71
= 20 X 0.425m =8.5 @2.09kg/m = 17.77kg
2856 | Steel fastener 8 mm X 75 mm | each | 40 | 7 | 280
2801 | MS Suspender 6 mm dia 0.75m long | each | 40 | 21 | 840
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 15566.38
| Cartage @ 1 % of A1 |  |  |  | 155.6638
LABOUR
1005 | Fitter, Grade 2 | day | 2 | 407 | 814
1010 | Mason, Grade 2 | day | 2 | 407 | 814
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 18822.0438
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2823.31
| Cost for 30 Metre |  |  |  | 21645.3538
| Rate per Metre |  |  |  | 721.5118
| Say |  |  |  | 722
722
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.10 | 450 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 832
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2710 | MS perforated cable tray painted with powder coating 450 X 62.5 X 2 mm | metre | 31.5 | 486 | 15309
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2726 | MS perforated cable tray Connector 450 X 62.5 X 2 mm | each | 9 | 49.38 | 444.42
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 20.9 | 37.8 | 790.02
= 20 X 0.5m =10 @2.09kg/m = 20.9kg
2855 | Steel fastener 6 mm X 75 mm | each | 40 | 5 | 200
2801 | MS Suspender 6 mm dia 0.75m long | each | 40 | 21 | 840
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 17663.44
| Cartage @ 1 % of A1 |  |  |  | 176.6344
LABOUR
1005 | Fitter, Grade 2 | day | 2.5 | 407 | 1017.5
1010 | Mason, Grade 2 | day | 2.5 | 407 | 1017.5
1007 | Khallasi | day | 5 | 368 | 1840
| TOTAL |  |  |  | 21715.0744
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3257.26
| Cost for 30 Metre |  |  |  | 24972.3344
| Rate per Metre |  |  |  | 832.4111
| Say |  |  |  | 832
832
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.11 | 600 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1008
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2711 | MS perforated cable tray painted with powder coating 600 X 62.5 X 2 mm | metre | 31.5 | 613.13 | 19313.6
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2727 | MS perforated cable tray Connector 600 X 62.5 X 2 mm | each | 9 | 54.14 | 487.26
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 27.17 | 37.8 | 1027.03
= 20 X 0.65m =13 @2.09kg/m = 27.17kg
2856 | Steel fastener 8 mm X 75 mm | each | 40 | 7 | 280
2802 | MS Suspender 8 mm dia 0.75m long | each | 40 | 25.52 | 1020.8
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 22208.69
| Cartage @ 1 % of A1 |  |  |  | 222.0869
LABOUR
1005 | Fitter, Grade 2 | day | 2.5 | 407 | 1017.5
1010 | Mason, Grade 2 | day | 2.5 | 407 | 1017.5
1007 | Khallasi | day | 5 | 368 | 1840
| TOTAL |  |  |  | 26305.7769
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3945.87
| Cost for 30 Metre |  |  |  | 30251.6469
| Rate per Metre |  |  |  | 1008.3882
| Say |  |  |  | 1008
1008
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.12 | 750 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1198
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2712 | MS perforated cable tray painted with powder coating 750 X 62.5 X 2 mm | metre | 31.5 | 759.38 | 23920.47
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2728 | MS perforated cable tray Connector 750 X 62.5 X 2 mm | each | 9 | 60.2 | 541.8
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 33.44 | 37.8 | 1264.03
= 20 X 0.8m =16 @2.09kg/m = 33.44kg
2856 | Steel fastener 8 mm X 75 mm | each | 40 | 7 | 280
2802 | MS Suspender 8 mm dia 0.75m long | each | 40 | 25.52 | 1020.8
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 27107.1
| Cartage @ 1 % of A1 |  |  |  | 271.071
LABOUR
1005 | Fitter, Grade 2 | day | 2.5 | 407 | 1017.5
1010 | Mason, Grade 2 | day | 2.5 | 407 | 1017.5
1007 | Khallasi | day | 5 | 368 | 1840
| TOTAL |  |  |  | 31253.171
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4687.98
| Cost for 30 Metre |  |  |  | 35941.151
| Rate per Metre |  |  |  | 1198.0384
| Say |  |  |  | 1198
1198
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.13 | 900 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1396
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2713 | MS perforated cable tray painted with powder coating 900 X 62.5 X 2 mm | metre | 31.5 | 888.75 | 27995.63
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2729 | MS perforated cable tray Connector 900 X 62.5 X 2 mm | each | 9 | 63.24 | 569.16
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 49.21 | 37.8 | 1860.14
= 20 X 0.95m =19 @2.59kg/m = 49.21kg
2856 | Steel fastener 8 mm X 75 mm | each | 40 | 7 | 280
2803 | MS Suspender 10 mm dia 0.75m long | each | 40 | 35.91 | 1436.4
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 32221.33
| Cartage @ 1 % of A1 |  |  |  | 322.2133
LABOUR
1005 | Fitter, Grade 2 | day | 2.5 | 407 | 1017.5
1010 | Mason, Grade 2 | day | 2.5 | 407 | 1017.5
1007 | Khallasi | day | 5 | 368 | 1840
| TOTAL |  |  |  | 36418.5433
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5462.78
| Cost for 30 Metre |  |  |  | 41881.3233
| Rate per Metre |  |  |  | 1396.0441
| Say |  |  |  | 1396
1396
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.14 | 600 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1032
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2714 | MS perforated cable tray painted with powder coating 600 X 75 X 2 mm | metre | 31.5 | 632.25 | 19915.88
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2727 | MS perforated cable tray Connector 600 X 62.5 X 2 mm | each | 9 | 54.14 | 487.26
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 27.17 | 37.8 | 1027.03
= 20 X 0.65m =13 @2.09kg/m = 27.17kg
2856 | Steel fastener 8 mm X 75 mm | each | 40 | 7 | 280
2802 | MS Suspender 8 mm dia 0.75m long | each | 40 | 25.52 | 1020.8
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 22810.97
| Cartage @ 1 % of A1 |  |  |  | 228.1097
LABOUR
1005 | Fitter, Grade 2 | day | 2.5 | 407 | 1017.5
1010 | Mason, Grade 2 | day | 2.5 | 407 | 1017.5
1007 | Khallasi | day | 5 | 368 | 1840
| TOTAL |  |  |  | 26914.0797
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4037.11
| Cost for 30 Metre |  |  |  | 30951.1897
| Rate per Metre |  |  |  | 1031.7063
| Say |  |  |  | 1032
1032
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.15 | 750 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1225
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2715 | MS perforated cable tray painted with powder coating 750 X 75 X 2 mm | metre | 31.5 | 781.88 | 24629.22
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2728 | MS perforated cable tray Connector 750 X 62.5 X 2 mm | each | 9 | 60.2 | 541.8
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 33.44 | 37.8 | 1264.03
= 20 X 0.8m =16 @2.09kg/m = 33.44kg
2856 | Steel fastener 8 mm X 75 mm | each | 40 | 7 | 280
2802 | MS Suspender 8 mm dia 0.75m long | each | 40 | 25.52 | 1020.8
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 27815.85
| Cartage @ 1 % of A1 |  |  |  | 278.1585
LABOUR
1005 | Fitter, Grade 2 | day | 2.5 | 407 | 1017.5
1010 | Mason, Grade 2 | day | 2.5 | 407 | 1017.5
1007 | Khallasi | day | 5 | 368 | 1840
| TOTAL |  |  |  | 31969.0085
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4795.35
| Cost for 30 Metre |  |  |  | 36764.3585
| Rate per Metre |  |  |  | 1225.4786
| Say |  |  |  | 1225
1225
Analysis of rate
4.1 | Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1.16 | 900 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1423
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2716 | MS perforated cable tray painted with powder coating 900 X 75 X 2 mm | metre | 31.5 | 911.25 | 28704.38
= 30 + 1.5 (Wastage @ 5%) = 31.5m
2729 | MS perforated cable tray Connector 900 X 62.5 X 2 mm | each | 9 | 63.24 | 569.16
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 49.21 | 37.8 | 1860.14
= 20 X 0.95m =19 @2.59kg/m = 49.21kg
2856 | Steel fastener 8 mm X 75 mm | each | 40 | 7 | 280
2803 | MS Suspender 10 mm dia 0.75m long | each | 40 | 35.91 | 1436.4
2936 | Painting with primer and finish paint | L.S. | 20 | 4 | 80
| Total cost of materials |  |  |  | 32930.08
| Cartage @ 1 % of A1 |  |  |  | 329.3008
LABOUR
1005 | Fitter, Grade 2 | day | 2.5 | 407 | 1017.5
1010 | Mason, Grade 2 | day | 2.5 | 407 | 1017.5
1007 | Khallasi | day | 5 | 368 | 1840
| TOTAL |  |  |  | 37134.3808
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5570.16
| Cost for 30 Metre |  |  |  | 42704.5408
| Rate per Metre |  |  |  | 1423.4847
| Say |  |  |  | 1423
1423
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.1 | 100 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 604
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2733 | MS perforated cable tray Bend 100 X 50 X 1.6 mm | each | 1 | 354.38 | 354.38
2717 | MS perforated cable tray Connector 100 X 50 X 1.6 mm | each | 1 | 26.85 | 26.85
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.17 | 37.8 | 6.43
= 1 X 0.15m =0.15 @1.11kg/m = 0.17kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 443.66
| Cartage @ 1 % of A1 |  |  |  | 4.4366
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 525.5966
| OVERHEADS & PROFIT @ 15 % |  |  |  | 78.84
| TOTAL |  |  |  | 604.4366
| Rate per Each |  |  |  | 604.4366
| Say |  |  |  | 604
604
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.2 | 150 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 714
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2734 | MS perforated cable tray Bend 150 X 50 X 1.6 mm | each | 1 | 438.75 | 438.75
2718 | MS perforated cable tray Connector 150 X 50 X 1.6 mm | each | 1 | 34.65 | 34.65
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.22 | 37.8 | 8.32
= 0.2 @ 1.11kg/m = 0.22kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 537.72
| Cartage @ 1 % of A1 |  |  |  | 5.3772
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 620.5972
| OVERHEADS & PROFIT @ 15 % |  |  |  | 93.09
| TOTAL |  |  |  | 713.6872
| Rate per Each |  |  |  | 713.6872
| Say |  |  |  | 714
714
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.3 | 200 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 868
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2735 | MS perforated cable tray Bend 225 X 50 X 1.6 mm | each | 1 | 568.13 | 568.13
2719 | MS perforated cable tray Connector 225 X 50 X 1.6 mm | each | 1 | 35.52 | 35.52
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.28 | 37.8 | 10.58
= 1 X 0.25m =0.25 @1.11kg/m = 0.28kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 670.23
| Cartage @ 1 % of A1 |  |  |  | 6.7023
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 754.4323
| OVERHEADS & PROFIT @ 15 % |  |  |  | 113.16
| TOTAL |  |  |  | 867.5923
| Rate per Each |  |  |  | 867.5923
| Say |  |  |  | 868
868
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.4 | 300 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 1023
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2736 | MS perforated cable tray Bend 300 X 50 X 1.6 mm | each | 1 | 697.5 | 697.5
2720 | MS perforated cable tray Connector 300 X 50 X 1.6 mm | each | 1 | 35.52 | 35.52
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.39 | 37.8 | 14.74
= 1 X 0.35m =0.35 @1.11kg/m = 0.39kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 803.76
| Cartage @ 1 % of A1 |  |  |  | 8.0376
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 889.2976
| OVERHEADS & PROFIT @ 15 % |  |  |  | 133.39
| TOTAL |  |  |  | 1022.6876
| Rate per Each |  |  |  | 1022.6876
| Say |  |  |  | 1023
1023
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.5 | 375 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1408
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2737 | MS perforated cable tray Bend 375 X 50 X 2 mm | each | 1 | 1006.88 | 1006.88
2721 | MS perforated cable tray Connector 375 X 50 X 2 mm | each | 1 | 38.98 | 38.98
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 0.9 | 37.8 | 34.02
= 1 X 0.425m =0.43 @2.09kg/m = 0.9kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1135.88
| Cartage @ 1 % of A1 |  |  |  | 11.3588
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1224.7388
| OVERHEADS & PROFIT @ 15 % |  |  |  | 183.71
| TOTAL |  |  |  | 1408.4488
| Rate per Each |  |  |  | 1408.4488
| Say |  |  |  | 1408
1408
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.6 | 450 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1617
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2738 | MS perforated cable tray Bend 450 X 50 X 2 mm | each | 1 | 1164.38 | 1164.38
2722 | MS perforated cable tray Connector 450 X 50 X 2 mm | each | 1 | 45.91 | 45.91
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.05 | 37.8 | 39.69
= 1 X 0.5m =0.5 @2.09kg/m = 1.05kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1315.02
| Cartage @ 1 % of A1 |  |  |  | 13.1502
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1405.6702
| OVERHEADS & PROFIT @ 15 % |  |  |  | 210.85
| TOTAL |  |  |  | 1616.5202
| Rate per Each |  |  |  | 1616.5202
| Say |  |  |  | 1617
1617
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.7 | 600 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2006
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2739 | MS perforated cable tray Bend 600 X 50 X 2 mm | each | 1 | 1479.38 | 1479.38
2723 | MS perforated cable tray Connector 600 X 50 X 2 mm | each | 1 | 50.25 | 50.25
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1650.08
| Cartage @ 1 % of A1 |  |  |  | 16.5008
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1744.0808
| OVERHEADS & PROFIT @ 15 % |  |  |  | 261.61
| TOTAL |  |  |  | 2005.6908
| Rate per Each |  |  |  | 2005.6908
| Say |  |  |  | 2006
2006
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.8 | 300 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1267
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2740 | MS perforated cable tray Bend 300 X 62.5 X 2 mm | each | 1 | 900 | 900
2724 | MS perforated cable tray Connector 300 X 62.5 X 2 mm | each | 1 | 38.98 | 38.98
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.39 | 37.8 | 14.74
= 0.35 @1.11kg/m = 0.39kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1013.72
| Cartage @ 1 % of A1 |  |  |  | 10.1372
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1101.3572
| OVERHEADS & PROFIT @ 15 % |  |  |  | 165.2
| TOTAL |  |  |  | 1266.5572
| Rate per Each |  |  |  | 1266.5572
| Say |  |  |  | 1267
1267
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.9 | 375 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1479
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2741 | MS perforated cable tray Bend 375 X 62.5 X 2 mm | each | 1 | 1057.5 | 1057.5
2725 | MS perforated cable tray Connector 375 X 62.5 X 2 mm | each | 1 | 45.05 | 45.05
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 0.9 | 37.8 | 34.02
= 1 X 0.425m =0.43 @2.09kg/m = 0.9kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1196.57
| Cartage @ 1 % of A1 |  |  |  | 11.9657
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1286.0357
| OVERHEADS & PROFIT @ 15 % |  |  |  | 192.91
| TOTAL |  |  |  | 1478.9457
| Rate per Each |  |  |  | 1478.9457
| Say |  |  |  | 1479
1479
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.10 | 450 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1722
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2742 | MS perforated cable tray Bend 450 X 62.5 X 2 mm | each | 1 | 1215 | 1215
2726 | MS perforated cable tray Connector 450 X 62.5 X 2 mm | each | 1 | 49.38 | 49.38
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.05 | 37.8 | 39.69
= 1 X 0.5m = @2.09kg/m = 1.05kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1360.07
| Cartage @ 1 % of A1 |  |  |  | 13.6007
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 1497.6707
| OVERHEADS & PROFIT @ 15 % |  |  |  | 224.65
| TOTAL |  |  |  | 1722.3207
| Rate per Each |  |  |  | 1722.3207
| Say |  |  |  | 1722
1722
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.11 | 600 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2129
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2743 | MS perforated cable tray Bend 600 X 62.5 X 2 mm | each | 1 | 1535.63 | 1535.63
2727 | MS perforated cable tray Connector 600 X 62.5 X 2 mm | each | 1 | 54.14 | 54.14
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @ 2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1710.22
| Cartage @ 1 % of A1 |  |  |  | 17.1022
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 1851.3222
| OVERHEADS & PROFIT @ 15 % |  |  |  | 277.7
| TOTAL |  |  |  | 2129.0222
| Rate per Each |  |  |  | 2129.0222
| Say |  |  |  | 2129
2129
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.12 | 750 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2574
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2744 | MS perforated cable tray Bend 750 X 62.5 X 2 mm | each | 1 | 1901.25 | 1901.25
2728 | MS perforated cable tray Connector 750 X 62.5 X 2 mm | each | 1 | 60.2 | 60.2
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.67 | 37.8 | 63.13
= 1 X 0.8m =0.8 @2.09kg/m = 1.67kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2093.62
| Cartage @ 1 % of A1 |  |  |  | 20.9362
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2238.5562
| OVERHEADS & PROFIT @ 15 % |  |  |  | 335.78
| TOTAL |  |  |  | 2574.3362
| Rate per Each |  |  |  | 2574.3362
| Say |  |  |  | 2574
2574
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.13 | 900 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2985
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2745 | MS perforated cable tray Bend 900 X 62.5 X 2 mm | each | 1 | 2221.88 | 2221.88
2729 | MS perforated cable tray Connector 900 X 62.5 X 2 mm | each | 1 | 63.24 | 63.24
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 2.46 | 37.8 | 92.99
= 1 X 0.95m =0.95 @2.59kg/m = 2.46kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2447.15
| Cartage @ 1 % of A1 |  |  |  | 24.4715
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2595.6215
| OVERHEADS & PROFIT @ 15 % |  |  |  | 389.34
| TOTAL |  |  |  | 2984.9615
| Rate per Each |  |  |  | 2984.9615
| Say |  |  |  | 2985
2985
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.14 | 600 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2181
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2746 | MS perforated cable tray Bend 600 X 75 X 2 mm | each | 1 | 1580.63 | 1580.63
2727 | MS perforated cable tray Connector 600 X 62.5 X 2 mm | each | 1 | 54.14 | 54.14
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1755.22
| Cartage @ 1 % of A1 |  |  |  | 17.5522
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 1896.7722
| OVERHEADS & PROFIT @ 15 % |  |  |  | 284.52
| TOTAL |  |  |  | 2181.2922
| Rate per Each |  |  |  | 2181.2922
| Say |  |  |  | 2181
2181
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.15 | 750 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2640
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2747 | MS perforated cable tray Bend 750 X 75 X 2 mm | each | 1 | 1957.5 | 1957.5
2728 | MS perforated cable tray Connector 750 X 62.5 X 2 mm | each | 1 | 60.2 | 60.2
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.67 | 37.8 | 63.13
= 1 X 0.8m =0.8 @2.09kg/m = 1.67kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2149.87
| Cartage @ 1 % of A1 |  |  |  | 21.4987
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2295.3687
| OVERHEADS & PROFIT @ 15 % |  |  |  | 344.31
| TOTAL |  |  |  | 2639.6787
| Rate per Each |  |  |  | 2639.6787
| Say |  |  |  | 2640
2640
Analysis of rate
4.2 | Supplying and installing following size of perforated pre-painted M.S. cable trays bends with perforation not more than 17.5%,, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.2.16 | 900 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 3025
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2748 | MS perforated cable tray Bend 900 X 75 X 2 mm | each | 1 | 2278.13 | 2278.13
2729 | MS perforated cable tray Connector 900 X 62.5 X 2 mm | each | 1 | 63.24 | 63.24
2806 | 35 mm X 35 mm X 5 mm angle iron | kg | 2.46 | 37.8 | 92.99
= 1 X 0.95m =0.95 @2.59kg/m = 2.46kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2503.4
| Cartage @ 1 % of A1 |  |  |  | 25.034
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 2630.354
| OVERHEADS & PROFIT @ 15 % |  |  |  | 394.55
| TOTAL |  |  |  | 3024.904
| Rate per Each |  |  |  | 3024.904
| Say |  |  |  | 3025
3025
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.1 | 100 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 683
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2765 | MS perforated cable tray Tee 100 X 50 X 1.6 mm | each | 1 | 421.88 | 421.88
2717 | MS perforated cable tray Connector 100 X 50 X 1.6 mm | each | 1 | 26.85 | 26.85
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.17 | 37.8 | 6.43
= 1 X 0.15m =0.15 @1.11kg/m = 0.17kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 511.16
| Cartage @ 1 % of A1 |  |  |  | 5.1116
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 593.7716
| OVERHEADS & PROFIT @ 15 % |  |  |  | 89.07
| TOTAL |  |  |  | 682.8416
| Rate per Each |  |  |  | 682.8416
| Say |  |  |  | 683
683
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.2 | 150 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 812
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2766 | MS perforated cable tray Tee 150 X 50 X 1.6 mm | each | 1 | 523.13 | 523.13
2718 | MS perforated cable tray Connector 150 X 50 X 1.6 mm | each | 1 | 34.65 | 34.65
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.22 | 37.8 | 8.32
= 0.2 @ 1.11kg/m = 0.22kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 622.1
| Cartage @ 1 % of A1 |  |  |  | 6.221
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 705.821
| OVERHEADS & PROFIT @ 15 % |  |  |  | 105.87
| TOTAL |  |  |  | 811.691
| Rate per Each |  |  |  | 811.691
| Say |  |  |  | 812
812
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.3 | 200 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 998
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2767 | MS perforated cable tray Tee 225 X 50 X 1.6 mm | each | 1 | 680.63 | 680.63
2719 | MS perforated cable tray Connector 225 X 50 X 1.6 mm | each | 1 | 35.52 | 35.52
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.28 | 37.8 | 10.58
= 1 X 0.25m =0.25 @1.11kg/m = 0.28kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 782.73
| Cartage @ 1 % of A1 |  |  |  | 7.8273
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 868.0573
| OVERHEADS & PROFIT @ 15 % |  |  |  | 130.21
| TOTAL |  |  |  | 998.2673
| Rate per Each |  |  |  | 998.2673
| Say |  |  |  | 998
998
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.4 | 300 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 1186
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2768 | MS perforated cable tray Tee 300 X 50 X 1.6 mm | each | 1 | 838.13 | 838.13
2720 | MS perforated cable tray Connector 300 X 50 X 1.6 mm | each | 1 | 35.52 | 35.52
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.39 | 37.8 | 14.74
= 1 X 0.35m =0.35 @1.11kg/m = 0.39kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 944.39
| Cartage @ 1 % of A1 |  |  |  | 9.4439
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1031.3339
| OVERHEADS & PROFIT @ 15 % |  |  |  | 154.7
| TOTAL |  |  |  | 1186.0339
| Rate per Each |  |  |  | 1186.0339
| Say |  |  |  | 1186
1186
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.5 | 375 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1637
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2769 | MS perforated cable tray Tee 375 X 50 X 2 mm | each | 1 | 1203.75 | 1203.75
2721 | MS perforated cable tray Connector 375 X 50 X 2 mm | each | 1 | 38.98 | 38.98
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 0.9 | 37.8 | 34.02
= 1 X 0.425m =0.43 @2.09kg/m = 0.9kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1332.75
| Cartage @ 1 % of A1 |  |  |  | 13.3275
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1423.5775
| OVERHEADS & PROFIT @ 15 % |  |  |  | 213.54
| TOTAL |  |  |  | 1637.1175
| Rate per Each |  |  |  | 1637.1175
| Say |  |  |  | 1637
1637
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.6 | 450 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1884
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2770 | MS perforated cable tray Tee 450 X 50 X 2 mm | each | 1 | 1395 | 1395
2722 | MS perforated cable tray Connector 450 X 50 X 2 mm | each | 1 | 45.91 | 45.91
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.05 | 37.8 | 39.69
= 1 X 0.5m =0.5 @2.09kg/m = 1.05kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1545.64
| Cartage @ 1 % of A1 |  |  |  | 15.4564
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1638.5964
| OVERHEADS & PROFIT @ 15 % |  |  |  | 245.79
| TOTAL |  |  |  | 1884.3864
| Rate per Each |  |  |  | 1884.3864
| Say |  |  |  | 1884
1884
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.7 | 600 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2345
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2771 | MS perforated cable tray Tee 600 X 50 X 2 mm | each | 1 | 1771.88 | 1771.88
2723 | MS perforated cable tray Connector 600 X 50 X 2 mm | each | 1 | 50.25 | 50.25
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1942.58
| Cartage @ 1 % of A1 |  |  |  | 19.4258
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 2039.5058
| OVERHEADS & PROFIT @ 15 % |  |  |  | 305.93
| TOTAL |  |  |  | 2345.4358
| Rate per Each |  |  |  | 2345.4358
| Say |  |  |  | 2345
2345
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.8 | 300 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1476
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2772 | MS perforated cable tray Tee 300 X 62.5 X 2 mm | each | 1 | 1080 | 1080
2724 | MS perforated cable tray Connector 300 X 62.5 X 2 mm | each | 1 | 38.98 | 38.98
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.39 | 37.8 | 14.74
= 0.35 @1.11kg/m = 0.39kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1193.72
| Cartage @ 1 % of A1 |  |  |  | 11.9372
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1283.1572
| OVERHEADS & PROFIT @ 15 % |  |  |  | 192.47
| TOTAL |  |  |  | 1475.6272
| Rate per Each |  |  |  | 1475.6272
| Say |  |  |  | 1476
1476
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.9 | 375 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1721
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2773 | MS perforated cable tray Tee 375 X 62.5 X 2 mm | each | 1 | 1265.63 | 1265.63
2725 | MS perforated cable tray Connector 375 X 62.5 X 2 mm | each | 1 | 45.05 | 45.05
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 0.9 | 37.8 | 34.02
= 1 X 0.425m =0.43 @2.09kg/m = 0.9kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1404.7
| Cartage @ 1 % of A1 |  |  |  | 14.047
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1496.247
| OVERHEADS & PROFIT @ 15 % |  |  |  | 224.44
| TOTAL |  |  |  | 1720.687
| Rate per Each |  |  |  | 1720.687
| Say |  |  |  | 1721
1721
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.10 | 450 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2003
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2774 | MS perforated cable tray Tee 450 X 62.5 X 2 mm | each | 1 | 1456.88 | 1456.88
2726 | MS perforated cable tray Connector 450 X 62.5 X 2 mm | each | 1 | 49.38 | 49.38
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.05 | 37.8 | 39.69
= 1 X 0.5m = @2.09kg/m = 1.05kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1601.95
| Cartage @ 1 % of A1 |  |  |  | 16.0195
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 1741.9695
| OVERHEADS & PROFIT @ 15 % |  |  |  | 261.3
| TOTAL |  |  |  | 2003.2695
| Rate per Each |  |  |  | 2003.2695
| Say |  |  |  | 2003
2003
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.11 | 600 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2482
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2775 | MS perforated cable tray Tee 600 X 62.5 X 2 mm | each | 1 | 1839.38 | 1839.38
2727 | MS perforated cable tray Connector 600 X 62.5 X 2 mm | each | 1 | 54.14 | 54.14
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @ 2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2013.97
| Cartage @ 1 % of A1 |  |  |  | 20.1397
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2158.1097
| OVERHEADS & PROFIT @ 15 % |  |  |  | 323.72
| TOTAL |  |  |  | 2481.8297
| Rate per Each |  |  |  | 2481.8297
| Say |  |  |  | 2482
2482
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.12 | 750 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 3012
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2776 | MS perforated cable tray Tee 750 X 62.5 X 2 mm | each | 1 | 2278.13 | 2278.13
2728 | MS perforated cable tray Connector 750 X 62.5 X 2 mm | each | 1 | 60.2 | 60.2
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.67 | 37.8 | 63.13
= 1 X 0.8m =0.8 @2.09kg/m = 1.67kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2470.5
| Cartage @ 1 % of A1 |  |  |  | 24.705
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2619.205
| OVERHEADS & PROFIT @ 15 % |  |  |  | 392.88
| TOTAL |  |  |  | 3012.085
| Rate per Each |  |  |  | 3012.085
| Say |  |  |  | 3012
3012
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.13 | 900 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 3501
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2777 | MS perforated cable tray Tee 900 X 62.5 X 2 mm | each | 1 | 2666.25 | 2666.25
2729 | MS perforated cable tray Connector 900 X 62.5 X 2 mm | each | 1 | 63.24 | 63.24
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 2.46 | 37.8 | 92.99
= 1 X 0.95m =0.95 @2.59kg/m = 2.46kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2891.52
| Cartage @ 1 % of A1 |  |  |  | 28.9152
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 3044.4352
| OVERHEADS & PROFIT @ 15 % |  |  |  | 456.67
| TOTAL |  |  |  | 3501.1052
| Rate per Each |  |  |  | 3501.1052
| Say |  |  |  | 3501
3501
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.14 | 600 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2554
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2778 | MS perforated cable tray Tee 600 X 75 X 2 mm | each | 1 | 1901.25 | 1901.25
2727 | MS perforated cable tray Connector 600 X 62.5 X 2 mm | each | 1 | 54.14 | 54.14
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2075.84
| Cartage @ 1 % of A1 |  |  |  | 20.7584
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2220.5984
| OVERHEADS & PROFIT @ 15 % |  |  |  | 333.09
| TOTAL |  |  |  | 2553.6884
| Rate per Each |  |  |  | 2553.6884
| Say |  |  |  | 2554
2554
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.15 | 750 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 3058
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2779 | MS perforated cable tray Tee 750 X 75 X 2 mm | each | 1 | 2317.5 | 2317.5
2728 | MS perforated cable tray Connector 750 X 62.5 X 2 mm | each | 1 | 60.2 | 60.2
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.67 | 37.8 | 63.13
= 1 X 0.8m =0.8 @2.09kg/m = 1.67kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2509.87
| Cartage @ 1 % of A1 |  |  |  | 25.0987
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2658.9687
| OVERHEADS & PROFIT @ 15 % |  |  |  | 398.85
| TOTAL |  |  |  | 3057.8187
| Rate per Each |  |  |  | 3057.8187
| Say |  |  |  | 3058
3058
Analysis of rate
4.3 | Supplying and installing following size of perforated pre-painted M.S. cable trays reducers with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.3.16 | 900 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 3574
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2780 | MS perforated cable tray Tee 900 X 75 X 2 mm | each | 1 | 2729.25 | 2729.25
2729 | MS perforated cable tray Connector 900 X 62.5 X 2 mm | each | 1 | 63.24 | 63.24
2806 | 35 mm X 35 mm X 5 mm angle iron | kg | 2.46 | 37.8 | 92.99
= 1 X 0.95m =0.95 @2.59kg/m = 2.46kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2954.52
| Cartage @ 1 % of A1 |  |  |  | 29.5452
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 3108.0652
| OVERHEADS & PROFIT @ 15 % |  |  |  | 466.21
| TOTAL |  |  |  | 3574.2752
| Rate per Each |  |  |  | 3574.2752
| Say |  |  |  | 3574
3574
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.1 | 100 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 683
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2781 | MS perforated cable tray Cross member 100 X 50 X 1.6 mm | each | 1 | 421.88 | 421.88
2717 | MS perforated cable tray Connector 100 X 50 X 1.6 mm | each | 1 | 26.85 | 26.85
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.17 | 37.8 | 6.43
= 1 X 0.15m =0.15 @1.11kg/m = 0.17kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 511.16
| Cartage @ 1 % of A1 |  |  |  | 5.1116
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 593.7716
| OVERHEADS & PROFIT @ 15 % |  |  |  | 89.07
| TOTAL |  |  |  | 682.8416
| Rate per Each |  |  |  | 682.8416
| Say |  |  |  | 683
683
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.2 | 150 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 812
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2782 | MS perforated cable tray Cross member 150 X 50 X 1.6 mm | each | 1 | 523.13 | 523.13
2718 | MS perforated cable tray Connector 150 X 50 X 1.6 mm | each | 1 | 34.65 | 34.65
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.22 | 37.8 | 8.32
= 0.2 @ 1.11kg/m = 0.22kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 622.1
| Cartage @ 1 % of A1 |  |  |  | 6.221
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 705.821
| OVERHEADS & PROFIT @ 15 % |  |  |  | 105.87
| TOTAL |  |  |  | 811.691
| Rate per Each |  |  |  | 811.691
| Say |  |  |  | 812
812
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.3 | 200 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 998
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2783 | MS perforated cable tray Cross member 225 X 50 X 1.6 mm | each | 1 | 680.63 | 680.63
2719 | MS perforated cable tray Connector 225 X 50 X 1.6 mm | each | 1 | 35.52 | 35.52
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.28 | 37.8 | 10.58
= 1 X 0.25m =0.25 @1.11kg/m = 0.28kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 782.73
| Cartage @ 1 % of A1 |  |  |  | 7.8273
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 868.0573
| OVERHEADS & PROFIT @ 15 % |  |  |  | 130.21
| TOTAL |  |  |  | 998.2673
| Rate per Each |  |  |  | 998.2673
| Say |  |  |  | 998
998
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.4 | 300 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 1186
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2784 | MS perforated cable tray Cross member 300 X 50 X 1.6 mm | each | 1 | 838.13 | 838.13
2720 | MS perforated cable tray Connector 300 X 50 X 1.6 mm | each | 1 | 35.52 | 35.52
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.39 | 37.8 | 14.74
= 1 X 0.35m =0.35 @1.11kg/m = 0.39kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 944.39
| Cartage @ 1 % of A1 |  |  |  | 9.4439
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1031.3339
| OVERHEADS & PROFIT @ 15 % |  |  |  | 154.7
| TOTAL |  |  |  | 1186.0339
| Rate per Each |  |  |  | 1186.0339
| Say |  |  |  | 1186
1186
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.5 | 375 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1637
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2785 | MS perforated cable tray Cross member 375 X 50 X 2 mm | each | 1 | 1203.75 | 1203.75
2721 | MS perforated cable tray Connector 375 X 50 X 2 mm | each | 1 | 38.98 | 38.98
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 0.9 | 37.8 | 34.02
= 1 X 0.425m =0.43 @2.09kg/m = 0.9kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1332.75
| Cartage @ 1 % of A1 |  |  |  | 13.3275
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1423.5775
| OVERHEADS & PROFIT @ 15 % |  |  |  | 213.54
| TOTAL |  |  |  | 1637.1175
| Rate per Each |  |  |  | 1637.1175
| Say |  |  |  | 1637
1637
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.6 | 450 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1884
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2786 | MS perforated cable tray Cross member 450 X 50 X 2 mm | each | 1 | 1395 | 1395
2722 | MS perforated cable tray Connector 450 X 50 X 2 mm | each | 1 | 45.91 | 45.91
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.05 | 37.8 | 39.69
= 1 X 0.5m =0.5 @2.09kg/m = 1.05kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1545.64
| Cartage @ 1 % of A1 |  |  |  | 15.4564
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1638.5964
| OVERHEADS & PROFIT @ 15 % |  |  |  | 245.79
| TOTAL |  |  |  | 1884.3864
| Rate per Each |  |  |  | 1884.3864
| Say |  |  |  | 1884
1884
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.7 | 600 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2345
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2787 | MS perforated cable tray Cross member 600 X 50 X 2 mm | each | 1 | 1771.88 | 1771.88
2723 | MS perforated cable tray Connector 600 X 50 X 2 mm | each | 1 | 50.25 | 50.25
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.358 | 37.8 | 51.33
= 1 X 0.65m =0.65 @2.09kg/m = 1.358kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1942.5
| Cartage @ 1 % of A1 |  |  |  | 19.425
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 2039.425
| OVERHEADS & PROFIT @ 15 % |  |  |  | 305.91
| TOTAL |  |  |  | 2345.335
| Rate per Each |  |  |  | 2345.335
| Say |  |  |  | 2345
2345
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.8 | 300 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1476
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2788 | MS perforated cable tray Cross member 300 X 62.5 X 2 mm | each | 1 | 1080 | 1080
2724 | MS perforated cable tray Connector 300 X 62.5 X 2 mm | each | 1 | 38.98 | 38.98
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.39 | 37.8 | 14.74
= 0.35 @1.11kg/m = 0.39kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1193.72
| Cartage @ 1 % of A1 |  |  |  | 11.9372
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1283.1572
| OVERHEADS & PROFIT @ 15 % |  |  |  | 192.47
| TOTAL |  |  |  | 1475.6272
| Rate per Each |  |  |  | 1475.6272
| Say |  |  |  | 1476
1476
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.9 | 375 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1721
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2789 | MS perforated cable tray Cross member 375 X 62.5 X 2 mm | each | 1 | 1265.63 | 1265.63
2725 | MS perforated cable tray Connector 375 X 62.5 X 2 mm | each | 1 | 45.05 | 45.05
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 0.9 | 37.8 | 34.02
= 1 X 0.425m =0.43 @2.09kg/m = 0.9kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1404.7
| Cartage @ 1 % of A1 |  |  |  | 14.047
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1496.247
| OVERHEADS & PROFIT @ 15 % |  |  |  | 224.44
| TOTAL |  |  |  | 1720.687
| Rate per Each |  |  |  | 1720.687
| Say |  |  |  | 1721
1721
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.10 | 450 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2003
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2790 | MS perforated cable tray Cross member 450 X 62.5 X 2 mm | each | 1 | 1456.88 | 1456.88
2726 | MS perforated cable tray Connector 450 X 62.5 X 2 mm | each | 1 | 49.38 | 49.38
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.05 | 37.8 | 39.69
= 1 X 0.5m = @2.09kg/m = 1.05kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1601.95
| Cartage @ 1 % of A1 |  |  |  | 16.0195
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 1741.9695
| OVERHEADS & PROFIT @ 15 % |  |  |  | 261.3
| TOTAL |  |  |  | 2003.2695
| Rate per Each |  |  |  | 2003.2695
| Say |  |  |  | 2003
2003
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.11 | 600 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2482
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2791 | MS perforated cable tray Cross member 600 X 62.5 X 2 mm | each | 1 | 1839.38 | 1839.38
2727 | MS perforated cable tray Connector 600 X 62.5 X 2 mm | each | 1 | 54.14 | 54.14
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @ 2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2013.97
| Cartage @ 1 % of A1 |  |  |  | 20.1397
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2158.1097
| OVERHEADS & PROFIT @ 15 % |  |  |  | 323.72
| TOTAL |  |  |  | 2481.8297
| Rate per Each |  |  |  | 2481.8297
| Say |  |  |  | 2482
2482
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.12 | 750 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 3012
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2792 | MS perforated cable tray Cross member 750 X 62.5 X 2 mm | each | 1 | 2278.13 | 2278.13
2728 | MS perforated cable tray Connector 750 X 62.5 X 2 mm | each | 1 | 60.2 | 60.2
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.67 | 37.8 | 63.13
= 1 X 0.8m =0.8 @2.09kg/m = 1.67kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2470.5
| Cartage @ 1 % of A1 |  |  |  | 24.705
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2619.205
| OVERHEADS & PROFIT @ 15 % |  |  |  | 392.88
| TOTAL |  |  |  | 3012.085
| Rate per Each |  |  |  | 3012.085
| Say |  |  |  | 3012
3012
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.13 | 900 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 3501
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2793 | MS perforated cable tray Cross member 900 X 62.5 X 2 mm | each | 1 | 2666.25 | 2666.25
2729 | MS perforated cable tray Connector 900 X 62.5 X 2 mm | each | 1 | 63.24 | 63.24
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 2.46 | 37.8 | 92.99
= 1 X 0.95m =0.95 @2.59kg/m = 2.46kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2891.52
| Cartage @ 1 % of A1 |  |  |  | 28.9152
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 3044.4352
| OVERHEADS & PROFIT @ 15 % |  |  |  | 456.67
| TOTAL |  |  |  | 3501.1052
| Rate per Each |  |  |  | 3501.1052
| Say |  |  |  | 3501
3501
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.14 | 600 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2554
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2794 | MS perforated cable tray Cross member 600 X 75 X 2 mm | each | 1 | 1901.25 | 1901.25
2727 | MS perforated cable tray Connector 600 X 62.5 X 2 mm | each | 1 | 54.14 | 54.14
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2075.84
| Cartage @ 1 % of A1 |  |  |  | 20.7584
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2220.5984
| OVERHEADS & PROFIT @ 15 % |  |  |  | 333.09
| TOTAL |  |  |  | 2553.6884
| Rate per Each |  |  |  | 2553.6884
| Say |  |  |  | 2554
2554
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.15 | 750 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 3058
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2795 | MS perforated cable tray Cross member 750 X 75 X 2 mm | each | 1 | 2317.5 | 2317.5
2728 | MS perforated cable tray Connector 750 X 62.5 X 2 mm | each | 1 | 60.2 | 60.2
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.67 | 37.8 | 63.13
= 1 X 0.8m =0.8 @2.09kg/m = 1.67kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2509.87
| Cartage @ 1 % of A1 |  |  |  | 25.0987
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2658.9687
| OVERHEADS & PROFIT @ 15 % |  |  |  | 398.85
| TOTAL |  |  |  | 3057.8187
| Rate per Each |  |  |  | 3057.8187
| Say |  |  |  | 3058
3058
Analysis of rate
4.4 | Supplying and installing following size of perforated pre-painted M.S. cable trays Tee's with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.4.16 | 900 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 3574
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2796 | MS perforated cable tray Cross member 900 X 75 X 2 mm | each | 1 | 2729.25 | 2729.25
2729 | MS perforated cable tray Connector 900 X 62.5 X 2 mm | each | 1 | 63.24 | 63.24
2806 | 35 mm X 35 mm X 5 mm angle iron | kg | 2.46 | 37.8 | 92.99
= 1 X 0.95m =0.95 @2.59kg/m = 2.46kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2954.52
| Cartage @ 1 % of A1 |  |  |  | 29.5452
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 3108.0652
| OVERHEADS & PROFIT @ 15 % |  |  |  | 466.21
| TOTAL |  |  |  | 3574.2752
| Rate per Each |  |  |  | 3574.2752
| Say |  |  |  | 3574
3574
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.1 | 100 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 661
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2749 | MS perforated cable tray Reducer 100 X 50 X 1.6 mm | each | 1 | 402.81 | 402.81
2717 | MS perforated cable tray Connector 100 X 50 X 1.6 mm | each | 1 | 26.85 | 26.85
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.17 | 37.8 | 6.43
= 1 X 0.15m =0.15 @1.11kg/m = 0.17kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 492.09
| Cartage @ 1 % of A1 |  |  |  | 4.9209
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 574.5109
| OVERHEADS & PROFIT @ 15 % |  |  |  | 86.18
| TOTAL |  |  |  | 660.6909
| Rate per Each |  |  |  | 660.6909
| Say |  |  |  | 661
661
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.2 | 150 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 774
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2750 | MS perforated cable tray Reducer 150 X 50 X 1.6 mm | each | 1 | 490.3 | 490.3
2718 | MS perforated cable tray Connector 150 X 50 X 1.6 mm | each | 1 | 34.65 | 34.65
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.22 | 37.8 | 8.32
= 0.2 @ 1.11kg/m = 0.22kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 589.27
| Cartage @ 1 % of A1 |  |  |  | 5.8927
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 672.6627
| OVERHEADS & PROFIT @ 15 % |  |  |  | 100.9
| TOTAL |  |  |  | 773.5627
| Rate per Each |  |  |  | 773.5627
| Say |  |  |  | 774
774
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.3 | 200 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 966
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2751 | MS perforated cable tray Reducer 225 X 50 X 1.6 mm | each | 1 | 648.82 | 648.82
2719 | MS perforated cable tray Connector 225 X 50 X 1.6 mm | each | 1 | 35.52 | 35.52
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.28 | 37.8 | 10.58
= 1 X 0.25m =0.25 @1.11kg/m = 0.28kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 754.92
| Cartage @ 1 % of A1 |  |  |  | 7.5492
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 839.9692
| OVERHEADS & PROFIT @ 15 % |  |  |  | 126
| TOTAL |  |  |  | 965.9692
| Rate per Each |  |  |  | 965.9692
| Say |  |  |  | 966
966
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.4 | 300 mm width X 50 mm depth X 1.6 mm thickness |  |  | DSR Rate Rs. | 1153
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2752 | MS perforated cable tray Reducer 300 X 50 X 1.6 mm | each | 1 | 805.62 | 805.62
2720 | MS perforated cable tray Connector 300 X 50 X 1.6 mm | each | 1 | 35.52 | 35.52
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.39 | 37.8 | 14.74
= 1 X 0.35m =0.35 @1.11kg/m = 0.39kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 915.88
| Cartage @ 1 % of A1 |  |  |  | 9.1588
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1002.5388
| OVERHEADS & PROFIT @ 15 % |  |  |  | 150.38
| TOTAL |  |  |  | 1152.9188
| Rate per Each |  |  |  | 1152.9188
| Say |  |  |  | 1153
1153
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.5 | 375 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1434
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2753 | MS perforated cable tray Reducer 375 X 50 X 2 mm | each | 1 | 1024.77 | 1024.77
2721 | MS perforated cable tray Connector 375 X 50 X 2 mm | each | 1 | 38.98 | 38.98
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 0.9 | 37.8 | 34.02
= 1 X 0.425m =0.43 @2.09kg/m = 0.9kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1157.77
| Cartage @ 1 % of A1 |  |  |  | 11.5777
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1246.8477
| OVERHEADS & PROFIT @ 15 % |  |  |  | 187.03
| TOTAL |  |  |  | 1433.8777
| Rate per Each |  |  |  | 1433.8777
| Say |  |  |  | 1434
1434
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.6 | 450 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1660
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2754 | MS perforated cable tray Reducer 450 X 50 X 2 mm | each | 1 | 1198.02 | 1198.02
2722 | MS perforated cable tray Connector 450 X 50 X 2 mm | each | 1 | 45.91 | 45.91
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.05 | 37.8 | 39.69
= 1 X 0.5m =0.5 @2.09kg/m = 1.05kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1352.66
| Cartage @ 1 % of A1 |  |  |  | 13.5266
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1443.6866
| OVERHEADS & PROFIT @ 15 % |  |  |  | 216.55
| TOTAL |  |  |  | 1660.2366
| Rate per Each |  |  |  | 1660.2366
| Say |  |  |  | 1660
1660
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.7 | 600 mm width X 50 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2020
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2755 | MS perforated cable tray Reducer 600 X 50 X 2 mm | each | 1 | 1491.69 | 1491.69
2723 | MS perforated cable tray Connector 600 X 50 X 2 mm | each | 1 | 50.25 | 50.25
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1662.39
| Cartage @ 1 % of A1 |  |  |  | 16.6239
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1756.5139
| OVERHEADS & PROFIT @ 15 % |  |  |  | 263.48
| TOTAL |  |  |  | 2019.9939
| Rate per Each |  |  |  | 2019.9939
| Say |  |  |  | 2020
2020
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.8 | 300 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1288
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2756 | MS perforated cable tray Reducer 300 X 62.5 X 2 mm | each | 1 | 918.23 | 918.23
2724 | MS perforated cable tray Connector 300 X 62.5 X 2 mm | each | 1 | 38.98 | 38.98
2804 | 25 mm X 25 mm X 3 mm angle iron | kg | 0.39 | 37.8 | 14.74
= 0.35 @1.11kg/m = 0.39kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1031.95
| Cartage @ 1 % of A1 |  |  |  | 10.3195
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1119.7695
| OVERHEADS & PROFIT @ 15 % |  |  |  | 167.97
| TOTAL |  |  |  | 1287.7395
| Rate per Each |  |  |  | 1287.7395
| Say |  |  |  | 1288
1288
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.9 | 375 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1505
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2757 | MS perforated cable tray Reducer 375 X 62.5 X 2 mm | each | 1 | 1080.21 | 1080.21
2725 | MS perforated cable tray Connector 375 X 62.5 X 2 mm | each | 1 | 45.05 | 45.05
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 0.9 | 37.8 | 34.02
= 1 X 0.425m =0.43 @2.09kg/m = 0.9kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1219.28
| Cartage @ 1 % of A1 |  |  |  | 12.1928
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1010 | Mason, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 1308.9728
| OVERHEADS & PROFIT @ 15 % |  |  |  | 196.35
| TOTAL |  |  |  | 1505.3228
| Rate per Each |  |  |  | 1505.3228
| Say |  |  |  | 1505
1505
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.10 | 450 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 1756
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2758 | MS perforated cable tray Reducer 450 X 62.5 X 2 mm | each | 1 | 1243.94 | 1243.94
2726 | MS perforated cable tray Connector 450 X 62.5 X 2 mm | each | 1 | 49.38 | 49.38
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.05 | 37.8 | 39.69
= 1 X 0.5m = @2.09kg/m = 1.05kg
2855 | Steel fastener 6 mm X 75 mm | each | 2 | 5 | 10
2801 | MS Suspender 6 mm dia 0.75m long | each | 2 | 21 | 42
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1389.01
| Cartage @ 1 % of A1 |  |  |  | 13.8901
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 1526.9001
| OVERHEADS & PROFIT @ 15 % |  |  |  | 229.04
| TOTAL |  |  |  | 1755.9401
| Rate per Each |  |  |  | 1755.9401
| Say |  |  |  | 1756
1756
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.11 | 600 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2173
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2759 | MS perforated cable tray Reducer 600 X 62.5 X 2 mm | each | 1 | 1573.11 | 1573.11
2727 | MS perforated cable tray Connector 600 X 62.5 X 2 mm | each | 1 | 54.14 | 54.14
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @ 2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1747.7
| Cartage @ 1 % of A1 |  |  |  | 17.477
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 1889.177
| OVERHEADS & PROFIT @ 15 % |  |  |  | 283.38
| TOTAL |  |  |  | 2172.557
| Rate per Each |  |  |  | 2172.557
| Say |  |  |  | 2173
2173
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.12 | 750 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2537
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2760 | MS perforated cable tray Reducer 750 X 62.5 X 2 mm | each | 1 | 1868.82 | 1868.82
2728 | MS perforated cable tray Connector 750 X 62.5 X 2 mm | each | 1 | 60.2 | 60.2
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.67 | 37.8 | 63.13
= 1 X 0.8m =0.8 @2.09kg/m = 1.67kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2061.19
| Cartage @ 1 % of A1 |  |  |  | 20.6119
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2205.8019
| OVERHEADS & PROFIT @ 15 % |  |  |  | 330.87
| TOTAL |  |  |  | 2536.6719
| Rate per Each |  |  |  | 2536.6719
| Say |  |  |  | 2537
2537
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.13 | 900 mm width X 62.5 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2995
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2761 | MS perforated cable tray Reducer 900 X 62.5 X 2 mm | each | 1 | 2230.59 | 2230.59
2729 | MS perforated cable tray Connector 900 X 62.5 X 2 mm | each | 1 | 63.24 | 63.24
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 2.46 | 37.8 | 92.99
= 1 X 0.95m =0.95 @2.59kg/m = 2.46kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2455.86
| Cartage @ 1 % of A1 |  |  |  | 24.5586
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2604.4186
| OVERHEADS & PROFIT @ 15 % |  |  |  | 390.66
| TOTAL |  |  |  | 2995.0786
| Rate per Each |  |  |  | 2995.0786
| Say |  |  |  | 2995
2995
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.14 | 600 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2235
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2762 | MS perforated cable tray Reducer 600 X 75 X 2 mm | each | 1 | 1626.82 | 1626.82
2727 | MS perforated cable tray Connector 600 X 62.5 X 2 mm | each | 1 | 54.14 | 54.14
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.36 | 37.8 | 51.41
= 1 X 0.65m =0.65 @2.09kg/m = 1.36kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1801.41
| Cartage @ 1 % of A1 |  |  |  | 18.0141
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 1943.4241
| OVERHEADS & PROFIT @ 15 % |  |  |  | 291.51
| TOTAL |  |  |  | 2234.9341
| Rate per Each |  |  |  | 2234.9341
| Say |  |  |  | 2235
2235
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.15 | 750 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 2591
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2763 | MS perforated cable tray Reducer 750 X 75 X 2 mm | each | 1 | 1915.28 | 1915.28
2728 | MS perforated cable tray Connector 750 X 62.5 X 2 mm | each | 1 | 60.2 | 60.2
2805 | 35 mm X 35 mm X 4 mm angle iron | kg | 1.67 | 37.8 | 63.13
= 1 X 0.8m =0.8 @2.09kg/m = 1.67kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2107.65
| Cartage @ 1 % of A1 |  |  |  | 21.0765
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2252.7265
| OVERHEADS & PROFIT @ 15 % |  |  |  | 337.91
| TOTAL |  |  |  | 2590.6365
| Rate per Each |  |  |  | 2590.6365
| Say |  |  |  | 2591
2591
Analysis of rate
4.5 | Supplying and installing following size of perforated pre-painted M.S. cable trays cross members with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.5.16 | 900 mm width X 75 mm depth X 2.0 mm thickness |  |  | DSR Rate Rs. | 3057
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2764 | MS perforated cable tray Reducer 900 X 75 X 2 mm | each | 1 | 2284.3 | 2284.3
2729 | MS perforated cable tray Connector 900 X 62.5 X 2 mm | each | 1 | 63.24 | 63.24
2806 | 35 mm X 35 mm X 5 mm angle iron | kg | 2.46 | 37.8 | 92.99
= 1 X 0.95m =0.95 @2.59kg/m = 2.46kg
2856 | Steel fastener 8 mm X 75 mm | each | 2 | 7 | 14
2802 | MS Suspender 8 mm dia 0.75m long | each | 2 | 25.52 | 51.04
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 2509.57
| Cartage @ 1 % of A1 |  |  |  | 25.0957
LABOUR
1005 | Fitter, Grade 2 | day | 0.08 | 407 | 32.56
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2658.6657
| OVERHEADS & PROFIT @ 15 % |  |  |  | 398.8
| TOTAL |  |  |  | 3057.4657
| Rate per Each |  |  |  | 3057.4657
| Say |  |  |  | 3057
3057
CHAPTER 5 – E A R T H I N G (Analysis of rate based on DAR)
Analysis of rate
5.1 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (but without charcoal/ coke and salt ) as required.
|  |  | DSR | Rate Rs. | 2846
Details of cost for one Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2826 | 40 mm dia. G.I. pipe (medium class) | metre | 4.73 | 207.95 | 983.6
= 4.50 + 0.23 (Wastage @ 5%) = 4.73m
2922 | CI/MS cover plate hinged to frame with Locking arrangement | each | 1 | 231 | 231
2836 | 40 mm to 20 mm reducer | each | 1 | 29 | 29
2918 | Funnel | each | 1 | 17 | 17
2919 | G.I. nuts and through bolts with washer | each | 1 | 22 | 22
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 50 | 3 | 150
2948 | Cement | tonne | 0.01 | 5250 | 52.5
2946 | Fine sand | cum | 0.03 | 672 | 20.16
| Total cost of materials |  |  |  | 1505.26
| Cartage @ 1 % of A1 |  |  |  | 15.0526
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
1010 | Mason, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 0.45 | 368 | 165.6
1083 | Drilling of 46 Nos 12 mm dia holes on G.I. pipe | L.S. | 1 | 300 | 300
| TOTAL |  |  |  | 2474.8126
| OVERHEADS & PROFIT @ 15 % |  |  |  | 371.22
| TOTAL |  |  |  | 2846.0326
| Rate per Set |  |  |  | 2846.0326
| Say |  |  |  | 2846
2846
Analysis of rate
5.2 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required.
|  |  | DSR | Rate Rs. | 3672
Details of cost for one Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2826 | 40 mm dia. G.I. pipe (medium class) | metre | 4.73 | 207.95 | 983.6
= 4.50 + 0.23 (Wastage @ 5%) = 4.73m
2922 | CI/MS cover plate hinged to frame with Locking arrangement | each | 1 | 231 | 231
2836 | 40 mm to 20 mm reducer | each | 1 | 29 | 29
2918 | Funnel | each | 1 | 17 | 17
2919 | G.I. nuts and through bolts with washer | each | 1 | 22 | 22
2941 | Charcoal | kg | 64 | 6.3 | 403.2
2943 | Salt | kg | 5 | 7 | 35
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 50 | 3 | 150
2948 | Cement | tonne | 0.01 | 5250 | 52.5
2946 | Fine sand | cum | 0.03 | 672 | 20.16
| Total cost of materials |  |  |  | 1943.46
| Cartage @ 1 % of A1 |  |  |  | 19.4346
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
1010 | Mason, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 1.2 | 368 | 441.6
1083 | Drilling of 46 Nos 12 mm dia holes on G.I. pipe | L.S. | 1 | 300 | 300
| TOTAL |  |  |  | 3193.3946
| OVERHEADS & PROFIT @ 15 % |  |  |  | 479.01
| TOTAL |  |  |  | 3672.4046
| Rate per Set |  |  |  | 3672.4046
| Say |  |  |  | 3672
3672
Analysis of rate
5.3 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. (but without charcoal/ coke and salt ) as required.
|  |  | DSR | Rate Rs. | 3583
Details of cost for one Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2915 | 600 mm X 600 mm X 6 mm thick G.I. plate | each | 1 | 1307 | 1307
2825 | 20 mm dia. G.I. pipe (medium class) | metre | 2.84 | 96.19 | 273.18
= 2.70 + 0.14 (Wastage @ 5%) = 2.84m
2922 | CI/MS cover plate hinged to frame with Locking arrangement | each | 1 | 231 | 231
2918 | Funnel | each | 1 | 17 | 17
2919 | G.I. nuts and through bolts with washer | each | 1 | 22 | 22
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 50 | 3 | 150
2948 | Cement | tonne | 0.01 | 5250 | 52.5
2946 | Fine sand | cum | 0.03 | 672 | 20.16
| Total cost of materials |  |  |  | 2072.84
| Cartage @ 1 % of A1 |  |  |  | 20.7284
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
1010 | Mason, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 1.45 | 368 | 533.6
| TOTAL |  |  |  | 3116.0684
| OVERHEADS & PROFIT @ 15 % |  |  |  | 467.41
| TOTAL |  |  |  | 3583.4784
| Rate per Set |  |  |  | 3583.4784
| Say |  |  |  | 3583
3583
Analysis of rate
5.4 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required.
|  |  | DSR | Rate Rs. | 4327
Details of cost for one Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2915 | 600 mm X 600 mm X 6 mm thick G.I. plate | each | 1 | 1307 | 1307
2825 | 20 mm dia. G.I. pipe (medium class) | metre | 2.84 | 96.19 | 273.18
= 2.70 + 0.14 (Wastage @ 5%) = 2.84m
2922 | CI/MS cover plate hinged to frame with Locking arrangement | each | 1 | 231 | 231
2918 | Funnel | each | 1 | 17 | 17
2919 | G.I. nuts and through bolts with washer | each | 1 | 22 | 22
2941 | Charcoal | kg | 96 | 6.3 | 604.8
2943 | Salt | kg | 5 | 7 | 35
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 50 | 3 | 150
2948 | Cement | tonne | 0.01 | 5250 | 52.5
2946 | Fine sand | cum | 0.03 | 672 | 20.16
| Total cost of materials |  |  |  | 2712.64
| Cartage @ 1 % of A1 |  |  |  | 27.1264
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
1010 | Mason, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 1.45 | 368 | 533.6
| TOTAL |  |  |  | 3762.2664
| OVERHEADS & PROFIT @ 15 % |  |  |  | 564.34
| TOTAL |  |  |  | 4326.6064
| Rate per Set |  |  |  | 4326.6064
| Say |  |  |  | 4327
4327
Analysis of rate
5.5 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. (but without charcoal/ coke and salt ) as required.
|  |  | DSR | Rate Rs. | 7546
Details of cost for one Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2905 | 600 mm X 600 mm X 3 mm thick copper plate (10.5 kg) | each | 1 | 4718.7 | 4718.7
2825 | 20 mm dia. G.I. pipe (medium class) | metre | 2.84 | 96.19 | 273.18
= 2.70 + 0.14 (Wastage @ 5%) = 2.84m
2922 | CI/MS cover plate hinged to frame with Locking arrangement | each | 1 | 231 | 231
2918 | Funnel | each | 1 | 17 | 17
2919 | G.I. nuts and through bolts with washer | each | 1 | 22 | 22
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 50 | 3 | 150
2948 | Cement | tonne | 0.01 | 5250 | 52.5
2946 | Fine sand | cum | 0.03 | 672 | 20.16
| Total cost of materials |  |  |  | 5484.54
| Cartage @ 1 % of A1 |  |  |  | 54.8454
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
1010 | Mason, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 1.45 | 368 | 533.6
| TOTAL |  |  |  | 6561.8854
| OVERHEADS & PROFIT @ 15 % |  |  |  | 984.28
| TOTAL |  |  |  | 7546.1654
| Rate per Set |  |  |  | 7546.1654
| Say |  |  |  | 7546
7546
Analysis of rate
5.6 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required.
|  |  | DSR | Rate Rs. | 8289
Details of cost for one Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2905 | 600 mm X 600 mm X 3 mm thick copper plate (10.5 kg) | each | 1 | 4718.7 | 4718.7
2825 | 20 mm dia. G.I. pipe (medium class) | metre | 2.84 | 96.19 | 273.18
= 2.70 + 0.14 (Wastage @ 5%) = 2.84m
2922 | CI/MS cover plate hinged to frame with Locking arrangement | each | 1 | 231 | 231
2918 | Funnel | each | 1 | 17 | 17
2919 | G.I. nuts and through bolts with washer | each | 1 | 22 | 22
2941 | Charcoal | kg | 96 | 6.3 | 604.8
2943 | Salt | kg | 5 | 7 | 35
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 50 | 3 | 150
2948 | Cement | tonne | 0.01 | 5250 | 52.5
2946 | Fine sand | cum | 0.03 | 672 | 20.16
| Total cost of materials |  |  |  | 6124.34
| Cartage @ 1 % of A1 |  |  |  | 61.2434
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
1010 | Mason, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 1.45 | 368 | 533.6
| TOTAL |  |  |  | 7208.0834
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1081.21
| TOTAL |  |  |  | 8289.2934
| Rate per Set |  |  |  | 8289.2934
| Say |  |  |  | 8289
8289
Analysis of rate
5.7 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required.
|  |  | DSR | Rate Rs. | 28
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2916 | 6 SWG G.I. wire | kg | 4.63 | 52.5 | 243.08
= 30x0.147 = 4.41 + 0.22 (Wastage @ 5%) = 4.63kg
1085 | Solder jointing | each | 2 | 12 | 24
| Total cost of materials |  |  |  | 267.08
| Cartage @ 1 % of A1 |  |  |  | 2.4308
LABOUR
1001 | Wireman | day | 0.125 | 447 | 55.88
1007 | Khallasi | day | 0.125 | 368 | 46
1012 | Beldar/ coolie | day | 1 | 368 | 368
| TOTAL |  |  |  | 739.3908
| OVERHEADS & PROFIT @ 15 % |  |  |  | 110.91
| Cost for 30 Metre |  |  |  | 850.3008
| Rate per Metre |  |  |  | 28.3434
| Say |  |  |  | 28
28
Analysis of rate
5.8 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm)
|  |  | DSR | Rate Rs. | 595
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2902 | 25 mm X 5 mm copper tape (1.15 kg/mtr) | kg | 34.5 | 430.5 | 14852.25
= 330x1.15 = 34.5 kg
1085 | Solder jointing | each | 5 | 12 | 60
| Total cost of materials |  |  |  | 14912.25
| Cartage @ 1 % of A1 |  |  |  | 148.5225
LABOUR
1001 | Wireman | day | 0.125 | 447 | 55.88
1007 | Khallasi | day | 0.125 | 368 | 46
1012 | Beldar/ coolie | day | 1 | 368 | 368
| TOTAL |  |  |  | 15530.6525
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2329.6
| Cost for 30 Metre |  |  |  | 17860.2525
| Rate per Metre |  |  |  | 595.3417
| Say |  |  |  | 595
595
Analysis of rate
5.9 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm)
|  |  | DSR | Rate Rs. | 85
Details of cost for 30 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2913 | 25 mm X 6 mm G.I. strip (1.2 kg/mtr) | kg | 37.8 | 42 | 1587.6
= 30x1.2 = 36.0 + 1.8 (Wastage @ 5%) = 37.8kg
1085 | Solder jointing | each | 5 | 12 | 60
| Total cost of materials |  |  |  | 1647.6
| Cartage @ 1 % of A1 |  |  |  | 15.876
LABOUR
1001 | Wireman | day | 0.125 | 447 | 55.88
1007 | Khallasi | day | 0.125 | 368 | 46
1002 | Cable jointer | day | 1 | 447 | 447
| TOTAL |  |  |  | 2212.356
| OVERHEADS & PROFIT @ 15 % |  |  |  | 331.85
| Cost for 30 Metre |  |  |  | 2544.206
| Rate per Metre |  |  |  | 84.8069
| Say |  |  |  | 85
85
Analysis of rate
5.10 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required.
|  |  | DSR | Rate Rs. | 872
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2902 | 25 mm X 5 mm copper tape (1.15 kg/mtr) | kg | 11.5 | 430.5 | 4950.75
= 10x1.15 = 11.5 kg
2826 | 40 mm dia. G.I. pipe (medium class) | metre | 10.5 | 207.95 | 2183.48
= 10.0 + 0.5 (Wastage @ 5%) = 10.5m
2838 | 40 mm dia. G.I. bend (medium class) | each | 1 | 51.45 | 51.45
| Total cost of materials |  |  |  | 7185.68
| Cartage @ 1 % of A1 |  |  |  | 71.8568
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
1012 | Beldar/ coolie | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 7582.7268
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1137.41
| Cost for 10 Metre |  |  |  | 8720.1368
| Rate per Metre |  |  |  | 872.0137
| Say |  |  |  | 872
872
Analysis of rate
5.11 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required.
|  |  | DSR | Rate Rs. | 351
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2912 | 25 mm X 5 mm G.I. strip (1.0 kg/mtr) | kg | 10.5 | 44.1 | 463.05
= 10x1.0 = 10.0 + 0.5 (Wastage @ 5%) = 10.5kg
2826 | 40 mm dia. G.I. pipe (medium class) | metre | 10.5 | 207.95 | 2183.48
= 10.0 + 0.5 (Wastage @ 5%) = 10.5m
2838 | 40 mm dia. G.I. bend (medium class) | each | 1 | 51.45 | 51.45
| Total cost of materials |  |  |  | 2697.98
| Cartage @ 1 % of A1 |  |  |  | 26.9798
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
1012 | Beldar/ coolie | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 3050.1498
| OVERHEADS & PROFIT @ 15 % |  |  |  | 457.52
| Cost for 10 Metre |  |  |  | 3507.6698
| Rate per Metre |  |  |  | 350.767
| Say |  |  |  | 351
351
Analysis of rate
5.12 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required.
|  |  | DSR | Rate Rs. | 134
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2824 | 15 mm dia. G.I. pipe (medium class) | metre | 10.5 | 76.24 | 800.52
= 10x1.0 = 10.0 + 0.5 (Wastage @ 5%) = 10.5kg
2916 | 6 SWG G.I. wire | kg | 1.79 | 52.5 | 93.98
= 10x0.147 = 1.47 + 0.09 (Wastage @ 5%) = 1.79kg
| Total cost of materials |  |  |  | 894.5
| Cartage @ 1 % of A1 |  |  |  | 8.945
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
1012 | Beldar/ coolie | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1163.435
| OVERHEADS & PROFIT @ 15 % |  |  |  | 174.52
| Cost for 10 Metre |  |  |  | 1337.955
| Rate per Metre |  |  |  | 133.7955
| Say |  |  |  | 134
134
Analysis of rate
5.13 | Providing and laying earth connection from earth electrode with 4.00 mm dia copper wire in 15 mm dia G.I. pipe from earth electrode including connection with copper thimble excavation and re-filling as required.
|  |  | DSR | Rate Rs. | 182
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2824 | 15 mm dia. G.I. pipe (medium class) | metre | 10.5 | 76.24 | 800.52
= 10x1.0 = 10.0 + 0.5 (Wastage @ 5%) = 10.5kg
2904 | 8 SWG copper wire (4.0 mm dia) | kg | 1.17 | 435.75 | 509.83
= ( 0.117 kg/mtr) = 10x0.117 = 1.17 kg
| Total cost of materials |  |  |  | 1310.35
| Cartage @ 1 % of A1 |  |  |  | 13.1035
LABOUR
1001 | Wireman | day | 0.17 | 447 | 75.99
1007 | Khallasi | day | 0.17 | 368 | 62.56
1012 | Beldar/ coolie | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1583.4435
| OVERHEADS & PROFIT @ 15 % |  |  |  | 237.52
| Cost for 10 Metre |  |  |  | 1820.9635
| Rate per Metre |  |  |  | 182.0963
| Say |  |  |  | 182
182
Analysis of rate
5.14 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required.
|  |  | DSR | Rate Rs. | 698
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2902 | 25 mm X 5 mm copper tape (1.15 kg/mtr) | kg | 11.5 | 430.5 | 4950.75
= 10x1.15 = 11.5 kg
2906 | Copper saddle | each | 17 | 26.25 | 446.25
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 34 | 0.4 | 13.6
2857 | PVC fastener 40mm long | each | 17 | 0.28 | 4.76
| Total cost of materials |  |  |  | 5415.36
| Cartage @ 1 % of A1 |  |  |  | 54.1536
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1010 | Mason, Grade 2 | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 6070.7636
| OVERHEADS & PROFIT @ 15 % |  |  |  | 910.61
| Cost for 10 Metre |  |  |  | 6981.3736
| Rate per Metre |  |  |  | 698.1374
| Say |  |  |  | 698
698
Analysis of rate
5.15 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required.
|  |  | DSR | Rate Rs. | 129
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2912 | 25 mm X 5 mm G.I. strip (1.0 kg/mtr) | kg | 10.5 | 44.1 | 463.05
= 10x1.0 = 10.0 + 0.5 (Wastage @ 5%) = 10.5kg
2917 | GI saddle 20mm x 3mm | each | 17 | 2 | 34
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 34 | 0.4 | 13.6
2857 | PVC fastener 40mm long | each | 17 | 0.28 | 4.76
| Total cost of materials |  |  |  | 515.41
| Cartage @ 1 % of A1 |  |  |  | 5.1541
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1010 | Mason, Grade 2 | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 1121.8141
| OVERHEADS & PROFIT @ 15 % |  |  |  | 168.27
| Cost for 10 Metre |  |  |  | 1290.0841
| Rate per Metre |  |  |  | 129.0084
| Say |  |  |  | 129
129
Analysis of rate
5.16 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required.
|  |  | DSR | Rate Rs. | 37
Details of cost for 50 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2916 | 6 SWG G.I. wire | kg | 7.72 | 52.5 | 405.3
= 50x0.147 = 7.35 + 0.37 (Wastage @ 5%) = 7.72kg
2921 | G.I. Hooks made of 8 SWG GI wire/ GI clip | each | 85 | 2 | 170
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
| Total cost of materials |  |  |  | 599.1
| Cartage @ 1 % of A1 |  |  |  | 5.991
LABOUR
1001 | Wireman | day | 0.75 | 447 | 335.25
1010 | Mason, Grade 2 | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 1.25 | 368 | 460
| TOTAL |  |  |  | 1603.841
| OVERHEADS & PROFIT @ 15 % |  |  |  | 240.58
| Cost for 50 Metre |  |  |  | 1844.421
| Rate per Metre |  |  |  | 36.8884
| Say |  |  |  | 37
37
Analysis of rate
5.17 | Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing as required.
|  |  | DSR | Rate Rs. | 87
Details of cost for 50 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2904 | 8 SWG copper wire (4.0 mm dia) | kg | 5.85 | 435.75 | 2549.14
(0.117 kg/mtr) = 50x0.117 = 5.85 kg
2921 | G.I. Hooks made of 8 SWG GI wire/ GI clip | each | 85 | 2 | 170
2857 | PVC fastener 40mm long | each | 85 | 0.28 | 23.8
| Total cost of materials |  |  |  | 2742.94
| Cartage @ 1 % of A1 |  |  |  | 27.4294
LABOUR
1001 | Wireman | day | 0.75 | 447 | 335.25
1010 | Mason, Grade 2 | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 1.25 | 368 | 460
| TOTAL |  |  |  | 3769.1194
| OVERHEADS & PROFIT @ 15 % |  |  |  | 565.37
| Cost for 50 Metre |  |  |  | 4334.4894
| Rate per Metre |  |  |  | 86.6898
| Say |  |  |  | 87
87
Analysis of rate
5.18 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required.
|  |  | DSR | Rate Rs. | 23
Details of cost for 50 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2916 | 6 SWG G.I. wire | kg | 7.72 | 52.5 | 405.3
(0.147 kg/mtr) = 50x0.147 = 7.35 + 0.37 (Wastage @ 5%) = 7.72kg
| Total cost of materials |  |  |  | 405.3
| Cartage @ 1 % of A1 |  |  |  | 4.053
LABOUR
1001 | Wireman | day | 0.75 | 447 | 335.25
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 1020.603
| OVERHEADS & PROFIT @ 15 % |  |  |  | 153.09
| Cost for 50 Metre |  |  |  | 1173.693
| Rate per Metre |  |  |  | 23.4739
| Say |  |  |  | 23
23
Analysis of rate
5.19 | Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required.
|  |  | DSR | Rate Rs. | 73
Details of cost for 50 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2904 | 8 SWG copper wire (4.0 mm dia) | kg | 5.85 | 435.75 | 2549.14
(0.117 kg/mtr) = 50x0.117 = 5.85 kg
| Total cost of materials |  |  |  | 2549.14
| Cartage @ 1 % of A1 |  |  |  | 25.4914
LABOUR
1001 | Wireman | day | 0.75 | 447 | 335.25
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 3185.8814
| OVERHEADS & PROFIT @ 15 % |  |  |  | 477.88
| Cost for 50 Metre |  |  |  | 3663.7614
| Rate per Metre |  |  |  | 73.2752
| Say |  |  |  | 73
73
Analysis of rate
5.20 | Providing and fixing earth bus of 50 mm X 5 mm copper strip on surface for connections etc. as required.
|  |  | DSR | Rate Rs. | 1283
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2907 | 50 mm X 5mm copper strip (2.30 kg/mtr) | kg | 23 | 430.5 | 9901.5
= 10x2.30 = 23.00 kg
2906 | Copper saddle | each | 17 | 26.25 | 446.25
2851 | Al. Alloy/ cadmium plated iron screws, 20 mm | each | 34 | 0.4 | 13.6
2857 | PVC fastener 40mm long | each | 17 | 0.28 | 4.76
| Total cost of materials |  |  |  | 10366.11
| Cartage @ 1 % of A1 |  |  |  | 103.6611
LABOUR
1001 | Wireman | day | 0.6 | 447 | 268.2
1010 | Mason, Grade 2 | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 0.85 | 368 | 312.8
| TOTAL |  |  |  | 11152.5211
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1672.88
| Cost for 10 Metre |  |  |  | 12825.4011
| Rate per Meter |  |  |  | 1282.5401
| Say |  |  |  | 1283
1283
CHAPTER 6 – LIGHTNING CONDUCTOR (Analysis of rate based on DAR)
Analysis of rate
6.1 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, copper tube, having single prong at top, with 85 mm dia 3 mm thick copper base plate including holes etc. complete as required.
|  |  | DSR | Rate Rs. | 0
Details of cost for One each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2909 | Lightning finial, 25 mm dia X 300 mm long, copper | each | 1 | 420 | 420
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
| Total cost of materials |  |  |  | 440
| Cartage @ 1 % of A1 |  |  |  | 4.4
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 571.6
| OVERHEADS & PROFIT @ 15 % |  |  |  | 85.74
| TOTAL |  |  |  | 657.34
| Rate per Each |  |  |  | 657.34
| Say |  |  |  | 657
657
Analysis of rate
6.2 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, G.I. tube, having single prong at top, with 85 mm dia 6 mm thick G.I. base plate including holes etc. complete as required.
|  |  | DSR | Rate Rs. | 304
Details of cost for One each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2910 | Lightning finial, 25 mm dia X 300 mm long, G.I. | each | 1 | 115.5 | 115.5
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
| Total cost of materials |  |  |  | 135.5
| Cartage @ 1 % of A1 |  |  |  | 1.355
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 264.055
| OVERHEADS & PROFIT @ 15 % |  |  |  | 39.61
| TOTAL |  |  |  | 303.665
| Rate per Each |  |  |  | 303.665
| Say |  |  |  | 304
304
Analysis of rate
6.3 | Fixing of lightning conductor finial (single prong) with base plate including holes etc. complete as required.
|  |  | DSR | Rate Rs. | 170
Details of cost for One each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
| Total cost of materials |  |  |  | 20
| Cartage @ 1 % of A1 |  |  |  | 0.2
LABOUR
1001 | Wireman | day | 0.08 | 447 | 35.76
1010 | Mason, Grade 2 | day | 0.08 | 407 | 32.56
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 147.4
| OVERHEADS & PROFIT @ 15 % |  |  |  | 22.11
| TOTAL |  |  |  | 169.51
| Rate per Each |  |  |  | 169.51
| Say |  |  |  | 170
170
Analysis of rate
6.4 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the finial or any other metallic object) by riveting / nut bolting/ sweating and soldering etc as required.
|  |  | DSR | Rate Rs. | 57
Details of cost for One each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2860 | 6 mm dia rivet/ stud/ bolts and nuts | each | 2 | 3 | 6
2940 | Tin solder etc. | L.S. | 1 | 5 | 5
| Total cost of materials |  |  |  | 11
| Cartage @ 1 % of A1 |  |  |  | 0.11
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.05 | 368 | 18.4
| TOTAL |  |  |  | 49.86
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7.48
| TOTAL |  |  |  | 57.34
| Rate per Each |  |  |  | 57.34
| Say |  |  |  | 57
57
Analysis of rate
6.5 | Providing and fixing copper tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For horizontal run)
|  |  | DSR | Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2901 | 20 mm X 3 mm copper tape ( 0.533 kg/mtr) | kg | 5.33 | 430.5 | 2294.57
= 10 m @ 0.533 kg/m = 5.33 kg
2917 | GI saddle 20mm x 3mm | each | 10 | 2 | 20
2857 | PVC fastener 40mm long | each | 10 | 0.28 | 2.8
2852 | Iron screws, 35 mm X 6 mm | each | 10 | 0.95 | 9.5
| Total cost of materials |  |  |  | 2326.87
| Cartage @ 1 % of A1 |  |  |  | 23.2687
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1010 | Mason, Grade 2 | day | 0.13 | 407 | 52.91
1007 | Khallasi | day | 0.38 | 368 | 139.84
| TOTAL |  |  |  | 2654.6387
| OVERHEADS & PROFIT @ 15 % |  |  |  | 398.2
| Cost for 10 Metre |  |  |  | 3052.8387
| Rate per Metre |  |  |  | 305.2839
| Say |  |  |  | 305
305
Analysis of rate
6.6 | Providing and fixing copper tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For vertical run)
|  |  | DSR | Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2901 | 20 mm X 3 mm copper tape ( 0.533 kg/mtr) | kg | 5.33 | 430.5 | 2294.57
= 10 m @ 0.533 kg/m = 5.33 kg
2917 | GI saddle 20mm x 3mm | each | 11 | 2 | 22
2857 | PVC fastener 40mm long | each | 11 | 0.28 | 3.08
2852 | Iron screws, 35 mm X 6 mm | each | 10 | 0.95 | 9.5
| Total cost of materials |  |  |  | 2329.15
| Cartage @ 1 % of A1 |  |  |  | 23.2915
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1010 | Mason, Grade 2 | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 2953.6915
| OVERHEADS & PROFIT @ 15 % |  |  |  | 443.05
| Cost for 10 Metre |  |  |  | 3396.7415
| Rate per Metre |  |  |  | 339.6741
| Say |  |  |  | 340
340
Analysis of rate
6.7 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For horizontal run)
|  |  | DSR | Rate Rs. | 66
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2911 | 20 mm X 3 mm G.I. Tape ( 0.461 kg/mtr) | kg | 4.84 | 48.3 | 233.77
=10+0.50(wastage@5%)=10.50m@0.461 kg/m=4.84 kg
2917 | GI saddle 20mm x 3mm | each | 10 | 2 | 20
2857 | PVC fastener 40mm long | each | 10 | 0.28 | 2.8
2852 | Iron screws, 35 mm X 6 mm | each | 10 | 0.95 | 9.5
| Total cost of materials |  |  |  | 266.07
| Cartage @ 1 % of A1 |  |  |  | 2.6607
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1010 | Mason, Grade 2 | day | 0.13 | 407 | 52.91
1007 | Khallasi | day | 0.38 | 368 | 139.84
| TOTAL |  |  |  | 573.2307
| OVERHEADS & PROFIT @ 15 % |  |  |  | 85.98
| Cost for 10 Metre |  |  |  | 659.2107
| Rate per Metre |  |  |  | 65.9211
| Say |  |  |  | 66
66
Analysis of rate
6.8 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For vertical run)
|  |  | DSR | Rate Rs. | 100
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2911 | 20 mm X 3 mm G.I. Tape ( 0.461 kg/mtr) | kg | 4.84 | 48.3 | 233.77
=10+0.50(wastage@5%)=10.50m@0.461 kg/m=4.84 kg
2917 | GI saddle 20mm x 3mm | each | 11 | 2 | 22
2857 | PVC fastener 40mm long | each | 11 | 0.28 | 3.08
2852 | Iron screws, 35 mm X 6 mm | each | 11 | 0.95 | 10.45
| Total cost of materials |  |  |  | 269.3
| Cartage @ 1 % of A1 |  |  |  | 2.693
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1010 | Mason, Grade 2 | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 873.243
| OVERHEADS & PROFIT @ 15 % |  |  |  | 130.99
| Cost for 10 Metre |  |  |  | 1004.233
| Rate per Metre |  |  |  | 100.4233
| Say |  |  |  | 100
100
Analysis of rate
6.9 | Fixing of copper/ G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For horizontal run)
|  |  | DSR | Rate Rs. | 39
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2917 | GI saddle 20mm x 3mm | each | 10 | 2 | 20
2857 | PVC fastener 40mm long | each | 10 | 0.28 | 2.8
2852 | Iron screws, 35 mm X 6 mm | each | 10 | 0.95 | 9.5
| Total cost of materials |  |  |  | 32.3
| Cartage @ 1 % of A1 |  |  |  | 0.323
LABOUR
1001 | Wireman | day | 0.25 | 447 | 111.75
1010 | Mason, Grade 2 | day | 0.13 | 407 | 52.91
1007 | Khallasi | day | 0.38 | 368 | 139.84
| TOTAL |  |  |  | 337.123
| OVERHEADS & PROFIT @ 15 % |  |  |  | 50.57
| Cost for 10 Metre |  |  |  | 387.693
| Rate per Metre |  |  |  | 38.7693
| Say |  |  |  | 39
39
Analysis of rate
6.10 | Fixing of copper/ G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For vertical run)
|  |  | DSR | Rate Rs. | 79
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2917 | GI saddle 20mm x 3mm | each | 11 | 2 | 22
2857 | PVC fastener 40mm long | each | 11 | 0.28 | 3.08
2935 | Cement, paint, sand etc. | L.S. | 11 | 4.5 | 49.5
2852 | Iron screws, 35 mm X 6 mm | each | 11 | 0.95 | 10.45
| Total cost of materials |  |  |  | 85.03
| Cartage @ 1 % of A1 |  |  |  | 0.8503
LABOUR
1001 | Wireman | day | 0.5 | 447 | 223.5
1010 | Mason, Grade 2 | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 0.75 | 368 | 276
| TOTAL |  |  |  | 687.1303
| OVERHEADS & PROFIT @ 15 % |  |  |  | 103.07
| Cost for 10 Metre |  |  |  | 790.2003
| Rate per Metre |  |  |  | 79.02
| Say |  |  |  | 79
79
Analysis of rate
6.11 | Providing and fixing testing joint, made of 20 mm X 3 mm thick copper strip, 125 mm long, with 4 nos. of tinned brass bolts, nuts, chuck nuts and spring washers etc. complete as required.
|  |  | DSR | Rate Rs. | 0
Details of cost for One each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2901 | 20 mm X 3 mm copper tape ( 0.533 kg/mtr) | kg | 0.066 | 430.5 | 28.41
= 0.125 m @ 0.533kg/m = 0.066 kg
2871 | 10 mm X 25 mm long tinned brass bolt with nut etc. | each | 4 | 27.5 | 110
| Total cost of materials |  |  |  | 138.41
| Cartage @ 1 % of A1 |  |  |  | 1.3841
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 164.2441
| OVERHEADS & PROFIT @ 15 % |  |  |  | 24.64
| TOTAL |  |  |  | 188.8841
| Rate per Each |  |  |  | 188.8841
| Say |  |  |  | 189
189
Analysis of rate
6.12 | Providing and fixing testing joint, made of 20 mm X 3 mm thick G.I. strip, 125 mm long, with 4 nos. of G.I. bolts, nuts, chuck nuts and spring washers etc. complete as required.
|  |  | DSR | Rate Rs. | 73
Details of cost for One each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2911 | 20 mm X 3 mm G.I. Tape ( 0.461 kg/mtr) | kg | 0.06 | 48.3 | 2.9
= 0.125 + 0.006 (Wastage @ 5%) = 0.131m @ 0.461kg/m = 0.067 kg
2866 | 10 mm X 25 mm long G.I. bolt with nut etc | each | 4 | 9 | 36
| Total cost of materials |  |  |  | 38.9
| Cartage @ 1 % of A1 |  |  |  | 0.389
LABOUR
1001 | Wireman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.03 | 368 | 11.04
| TOTAL |  |  |  | 63.739
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9.56
| TOTAL |  |  |  | 73.299
| Rate per Each |  |  |  | 73.299
| Say |  |  |  | 73
73
Analysis of rate
6.13 | Providing and laying copper tape 32 mm X 6 mm from earth electrode directly in ground as required.
|  |  | DSR | Rate Rs. | 0
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2903 | 32 mm X 6 mm copper tape ( 1.705 kg/mtr) | kg | 17.05 | 430.5 | 7340.03
= 10 m @ 1.705 kg/m = 17.05 kg
| Total cost of materials |  |  |  | 7340.03
| Cartage @ 1 % of A1 |  |  |  | 73.4003
LABOUR
1001 | Wireman | day | 0.165 | 447 | 73.76
1007 | Khallasi | day | 0.165 | 368 | 60.72
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 7731.9103
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1159.79
| Cost for 10 Metre |  |  |  | 8891.7003
| Rate per Metre |  |  |  | 889.17
| Say |  |  |  | 889
889
Analysis of rate
6.14 | Providing and laying G.I. tape 32 mm X 6 mm from earth electrode directly in ground as required.
|  |  | DSR | Rate Rs. | 112
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2914 | 32 mm X 6 mm G.I. Tape ( 1.475 kg/mtr) | kg | 15.49 | 42 | 650.58
= 10 + 0.50 (wastage @ 5%) = 10.50m @ 1.475 kg/m = 15.49 kg
| Total cost of materials |  |  |  | 650.58
| Cartage @ 1 % of A1 |  |  |  | 6.5058
LABOUR
1001 | Wireman | day | 0.165 | 447 | 73.76
1007 | Khallasi | day | 0.165 | 368 | 60.72
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 975.5658
| OVERHEADS & PROFIT @ 15 % |  |  |  | 146.33
| Cost for 10 Metre |  |  |  | 1121.8958
| Rate per Metre |  |  |  | 112.1896
| Say |  |  |  | 112
112
Analysis of rate
6.15 | Laying copper/ G.I. tape 32 mm X 6 mm from earth electrode directly in ground as required.
|  |  | DSR | Rate Rs. | 37
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 0.165 | 447 | 73.76
1007 | Khallasi | day | 0.165 | 368 | 60.72
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 318.48
| OVERHEADS & PROFIT @ 15 % |  |  |  | 47.77
| Cost for 10 Metre |  |  |  | 366.25
| Rate per Metre |  |  |  | 36.625
| Say |  |  |  | 37
37
CHAPTER 7 – MV CABLE LAYING (Analysis of rate based on DAR)
Analysis of rate
7.1 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
7.1.1 | Upto 35 sq. mm |  |  | DSR Rate Rs. | 206
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 8.76 | 672 | 5886.72
| Total cost of materials |  |  |  | 8640.72
| Cartage @ 1 % of A1 |  |  |  | 86.4072
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 10646.1272
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1596.92
| TOTAL |  |  |  | 12243.0472
14.4 | Excavation including refilling as required | cum | 26.26 | 318 | 8350.68
| Cost for 100 Meters |  |  |  | 20593.7272
| Rate per Meter |  |  |  | 205.9373
| Say |  |  |  | 206
206
Analysis of rate
7.1 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
7.1.2 | Above 35 sq. mm and upto 95 sq. mm |  |  | DSR Rate Rs. | 214
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 8.76 | 672 | 5886.72
| Total cost of materials |  |  |  | 8640.72
| Cartage @ 1 % of A1 |  |  |  | 86.4072
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 6 | 368 | 2208
| TOTAL |  |  |  | 11382.1272
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1707.32
| TOTAL |  |  |  | 13089.4472
14.4 | Excavation including refilling as required | cum | 26.26 | 318 | 8350.68
| Cost for 100 Meters |  |  |  | 21440.1272
| Rate per Meter |  |  |  | 214.4013
| Say |  |  |  | 214
214
Analysis of rate
7.1 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
7.1.3 | Above 95 sq. mm and upto 185 sq. mm |  |  | DSR Rate Rs. | 223
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 8.76 | 672 | 5886.72
| Total cost of materials |  |  |  | 8640.72
| Cartage @ 1 % of A1 |  |  |  | 86.4072
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 8 | 368 | 2944
| TOTAL |  |  |  | 12118.1272
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1817.72
| TOTAL |  |  |  | 13935.8472
14.4 | Excavation including refilling as required | cum | 26.26 | 318 | 8350.68
| Cost for 100 Meters |  |  |  | 22286.5272
| Rate per Meter |  |  |  | 222.8653
| Say |  |  |  | 223
223
Analysis of rate
7.1 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
7.1.4 | Above 185 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 248
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 8.76 | 672 | 5886.72
| Total cost of materials |  |  |  | 8640.72
| Cartage @ 1 % of A1 |  |  |  | 86.4072
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 14 | 368 | 5152
| TOTAL |  |  |  | 14326.1272
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2148.92
| TOTAL |  |  |  | 16475.0472
14.4 | Excavation including refilling as required | cum | 26.26 | 318 | 8350.68
| Cost for 100 Meters |  |  |  | 24825.7272
| Rate per Meter |  |  |  | 248.2573
| Say |  |  |  | 248
248
Analysis of rate
7.2 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
7.2.1 | Upto 35 sq. mm |  |  | DSR Rate Rs. | 141
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 5 | 672 | 3360
| Total cost of materials |  |  |  | 6114
| Cartage @ 1 % of A1 |  |  |  | 61.14
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 8094.14
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1214.12
| TOTAL |  |  |  | 9308.26
14.4 | Excavation including refilling as required | cum | 15 | 318 | 4770
| Cost for 100 Meters |  |  |  | 14078.26
| Rate per Meter |  |  |  | 140.7826
| Say |  |  |  | 141
141
Analysis of rate
7.2 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
7.2.2 | Above 35 sq. mm and upto 95 sq. mm |  |  | DSR Rate Rs. | 149
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 5 | 672 | 3360
| Total cost of materials |  |  |  | 6114
| Cartage @ 1 % of A1 |  |  |  | 61.14
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 6 | 368 | 2208
| TOTAL |  |  |  | 8830.14
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1324.52
| TOTAL |  |  |  | 10154.66
14.4 | Excavation including refilling as required | cum | 15 | 318 | 4770
| Cost for 100 Meters |  |  |  | 14924.66
| Rate per Meter |  |  |  | 149.2466
| Say |  |  |  | 149
149
Analysis of rate
7.2 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
7.2.3 | Above 95 sq. mm and upto 185 sq. mm |  |  | DSR Rate Rs. | 158
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 5 | 672 | 3360
| Total cost of materials |  |  |  | 6114
| Cartage @ 1 % of A1 |  |  |  | 61.14
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 8 | 368 | 2944
| TOTAL |  |  |  | 9566.14
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1434.92
| TOTAL |  |  |  | 11001.06
14.4 | Excavation including refilling as required | cum | 15 | 318 | 4770
| Cost for 100 Meters |  |  |  | 15771.06
| Rate per Meter |  |  |  | 157.7106
| Say |  |  |  | 158
158
Analysis of rate
7.2 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
7.2.4 | Above 185 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 183
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 5 | 672 | 3360
| Total cost of materials |  |  |  | 6114
| Cartage @ 1 % of A1 |  |  |  | 61.14
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 14 | 368 | 5152
| TOTAL |  |  |  | 11774.14
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1766.12
| TOTAL |  |  |  | 13540.26
14.4 | Excavation including refilling as required | cum | 15 | 318 | 4770
| Cost for 100 Meters |  |  |  | 18310.26
| Rate per Meter |  |  |  | 183.1026
| Say |  |  |  | 183
183
Analysis of rate
7.3 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering.
7.3.1 | Upto 35 sq. mm |  |  | DSR Rate Rs. | 97
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 1183
| OVERHEADS & PROFIT @ 15 % |  |  |  | 177.45
| TOTAL |  |  |  | 1360.45
14.4 | Excavation including refilling as required | cum | 26.26 | 318 | 8350.68
| Cost for 100 Meters |  |  |  | 9711.13
| Rate per Meter |  |  |  | 97.1113
| Say |  |  |  | 97
97
Analysis of rate
7.3 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering.
7.3.2 | Above 35 sq. mm and upto 95 sq. mm |  |  | DSR Rate Rs. | 106
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 1919
| OVERHEADS & PROFIT @ 15 % |  |  |  | 287.85
| TOTAL |  |  |  | 2206.85
14.4 | Excavation including refilling as required | cum | 26.26 | 318 | 8350.68
| Cost for 100 Meters |  |  |  | 10557.53
| Rate per Meter |  |  |  | 105.5753
| Say |  |  |  | 106
106
Analysis of rate
7.3 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering.
7.3.3 | Above 95 sq. mm and upto 185 sq. mm |  |  | DSR Rate Rs. | 114
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 6 | 368 | 2208
| TOTAL |  |  |  | 2655
| OVERHEADS & PROFIT @ 15 % |  |  |  | 398.25
| TOTAL |  |  |  | 3053.25
14.4 | Excavation including refilling as required | cum | 26.26 | 318 | 8350.68
| Cost for 100 Meters |  |  |  | 11403.93
| Rate per Meter |  |  |  | 114.0393
| Say |  |  |  | 114
114
Analysis of rate
7.3 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering.
7.3.4 | Above 185 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 139
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 12 | 368 | 4416
| TOTAL |  |  |  | 4863
| OVERHEADS & PROFIT @ 15 % |  |  |  | 729.45
| TOTAL |  |  |  | 5592.45
14.4 | Excavation including refilling as required | cum | 26.26 | 318 | 8350.68
| Cost for 100 Meters |  |  |  | 13943.13
| Rate per Meter |  |  |  | 139.4313
| Say |  |  |  | 139
139
Analysis of rate
7.4 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering.
7.4.1 | Upto 35 sq. mm |  |  | DSR Rate Rs. | 61
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 1183
| OVERHEADS & PROFIT @ 15 % |  |  |  | 177.45
| TOTAL |  |  |  | 1360.45
14.4 | Excavation including refilling as required | cum | 15 | 318 | 4770
| Cost for 100 Meters |  |  |  | 6130.45
| Rate per Meter |  |  |  | 61.3045
| Say |  |  |  | 61
61
Analysis of rate
7.4 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering.
7.4.2 | Above 35 sq. mm and upto 95 sq. mm |  |  | DSR Rate Rs. | 70
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 1919
| OVERHEADS & PROFIT @ 15 % |  |  |  | 287.85
| TOTAL |  |  |  | 2206.85
14.4 | Excavation including refilling as required | cum | 15 | 318 | 4770
| Cost for 100 Meters |  |  |  | 6976.85
| Rate per Meter |  |  |  | 69.7685
| Say |  |  |  | 70
70
Analysis of rate
7.4 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering.
7.4.3 | Above 95 sq. mm and upto 185 sq. mm |  |  | DSR Rate Rs. | 78
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 6 | 368 | 2208
| TOTAL |  |  |  | 2655
| OVERHEADS & PROFIT @ 15 % |  |  |  | 398.25
| TOTAL |  |  |  | 3053.25
14.4 | Excavation including refilling as required | cum | 15 | 318 | 4770
| Cost for 100 Meters |  |  |  | 7823.25
| Rate per Meter |  |  |  | 78.2325
| Say |  |  |  | 78
78
Analysis of rate
7.4 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering.
7.4.4 | Above 185 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 104
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 12 | 368 | 4416
| TOTAL |  |  |  | 4863
| OVERHEADS & PROFIT @ 15 % |  |  |  | 729.45
| TOTAL |  |  |  | 5592.45
14.4 | Excavation including refilling as required | cum | 15 | 318 | 4770
| Cost for 100 Meters |  |  |  | 10362.45
| Rate per Meter |  |  |  | 103.6245
| Say |  |  |  | 104
104
Analysis of rate
7.5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
7.5.1 | Upto 35 sq. mm |  |  | DSR Rate Rs. | 18
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 1551
| OVERHEADS & PROFIT @ 15 % |  |  |  | 232.65
| Cost for 100 Meters |  |  |  | 1783.65
| Rate per Meter |  |  |  | 17.8365
| Say |  |  |  | 18
18
Analysis of rate
7.5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
7.5.2 | Above 35 sq. mm and upto 95 sq. mm |  |  | DSR Rate Rs. | 28
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1.25 | 447 | 558.75
1007 | Khallasi | day | 5 | 368 | 1840
| TOTAL |  |  |  | 2398.75
| OVERHEADS & PROFIT @ 15 % |  |  |  | 359.81
| Cost for 100 Meters |  |  |  | 2758.56
| Rate per Meter |  |  |  | 27.5856
| Say |  |  |  | 28
28
Analysis of rate
7.5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
7.5.3 | Above 95 sq. mm and upto 185 sq. mm |  |  | DSR Rate Rs. | 37
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 7 | 368 | 2576
| TOTAL |  |  |  | 3246.5
| OVERHEADS & PROFIT @ 15 % |  |  |  | 486.98
| Cost for 100 Meters |  |  |  | 3733.48
| Rate per Meter |  |  |  | 37.3348
| Say |  |  |  | 37
37
Analysis of rate
7.5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
7.5.4 | Above 185 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 65
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1007 | Khallasi | day | 13 | 368 | 4784
| TOTAL |  |  |  | 5678
| OVERHEADS & PROFIT @ 15 % |  |  |  | 851.7
| Cost for 100 Meters |  |  |  | 6529.7
| Rate per Meter |  |  |  | 65.297
| Say |  |  |  | 65
65
Analysis of rate
7.6 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
7.6.1 | Upto 35 sq. mm |  |  | DSR Rate Rs. | 14
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 1183
| OVERHEADS & PROFIT @ 15 % |  |  |  | 177.45
| Cost for 100 Meters |  |  |  | 1360.45
| Rate per Meter |  |  |  | 13.6045
| Say |  |  |  | 14
14
Analysis of rate
7.6 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
7.6.2 | Above 35 sq. mm and upto 95 sq. mm |  |  | DSR Rate Rs. | 22
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 1919
| OVERHEADS & PROFIT @ 15 % |  |  |  | 287.85
| Cost for 100 Meters |  |  |  | 2206.85
| Rate per Meter |  |  |  | 22.0685
| Say |  |  |  | 22
22
Analysis of rate
7.6 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
7.6.3 | Above 95 sq. mm and upto 185 sq. mm |  |  | DSR Rate Rs. | 31
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 6 | 368 | 2208
| TOTAL |  |  |  | 2655
| OVERHEADS & PROFIT @ 15 % |  |  |  | 398.25
| Cost for 100 Meters |  |  |  | 3053.25
| Rate per Meter |  |  |  | 30.5325
| Say |  |  |  | 31
31
Analysis of rate
7.6 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
7.6.4 | Above 185 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 56
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 12 | 368 | 4416
| TOTAL |  |  |  | 4863
| OVERHEADS & PROFIT @ 15 % |  |  |  | 729.45
| Cost for 100 Meters |  |  |  | 5592.45
| Rate per Meter |  |  |  | 55.9245
| Say |  |  |  | 56
56
Analysis of rate
7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
7.7.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) |  |  | DSR Rate Rs. | 25
Details of cost for 100 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2881 | GI saddles 19mm x 0.55mm for conduit | each | 226 | 0.85 | 192.1
= 100/0.45 = 222 + 4 (Wastage @ 2%) = 226 Nos
2854 | Iron screws, 45 mm X 6 mm | each | 452 | 1 | 452
2857 | PVC fastener 40mm long | each | 452 | 0.28 | 126.56
2935 | Cement, paint, sand etc. | L.S. | 2 | 4.5 | 9
| Total cost of materials |  |  |  | 779.66
| Cartage @ 1 % of A1 |  |  |  | 7.7966
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1010 | Mason, Grade 2 | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 2173.9566
| OVERHEADS & PROFIT @ 15 % |  |  |  | 326.09
| Cost for 100 Metre |  |  |  | 2500.0466
| Rate per Metre |  |  |  | 25.0005
| Say |  |  |  | 25
25
Analysis of rate
7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
7.7.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) |  |  | DSR Rate Rs. | 72
Details of cost for 100 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2862 | 32mm X 8mm bolts & nuts | each | 350 | 4 | 1400
= 2x(100/0.6) = 334 + 16 (Wastage @ 5%) = 350 Nos
2809 | 20/25 mm X 3 mm flat iron | kg | 9.06 | 37.8 | 342.47
= 84 x 0.16m = 13.44m @ 0.337kg/m = 4.53 kg
2855 | Steel fastener 6 mm X 75 mm | each | 336 | 5 | 1680
| Total cost of materials |  |  |  | 3422.47
| Cartage @ 1 % of A1 |  |  |  | 34.2247
LABOUR
1001 | Wireman | day | 1.25 | 447 | 558.75
1005 | Fitter, Grade 2 | day | 0.33 | 407 | 134.31
1009 | Blacksmith, Grade 2 | day | 0.33 | 407 | 134.31
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1007 | Khallasi | day | 5 | 368 | 1840
| TOTAL |  |  |  | 6258.3747
| OVERHEADS & PROFIT @ 15 % |  |  |  | 938.76
| Cost for 100 Metre |  |  |  | 7197.1347
| Rate per Metre |  |  |  | 71.9713
| Say |  |  |  | 72
72
Analysis of rate
7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
7.7.3 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) |  |  | DSR Rate Rs. | 84
Details of cost for 100 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2862 | 32mm X 8mm bolts & nuts | each | 350 | 4 | 1400
= 2x(100/0.6) = 334 + 16 (Wastage @ 5%) = 350 Nos
2809 | 20/25 mm X 3 mm flat iron | kg | 13.58 | 37.8 | 513.32
= 84 x 0.24m = 20.16m @ 0.337kg/m = 6.79 kg
2855 | Steel fastener 6 mm X 75 mm | each | 336 | 5 | 1680
| Total cost of materials |  |  |  | 3593.32
| Cartage @ 1 % of A1 |  |  |  | 35.9332
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1005 | Fitter, Grade 2 | day | 0.33 | 407 | 134.31
1009 | Blacksmith, Grade 2 | day | 0.33 | 407 | 134.31
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1007 | Khallasi | day | 7 | 368 | 2576
| TOTAL |  |  |  | 7278.6832
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1091.8
| Cost for 100 Metre |  |  |  | 8370.4832
| Rate per Metre |  |  |  | 83.7048
| Say |  |  |  | 84
84
Analysis of rate
7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
7.7.4 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) |  |  | DSR Rate Rs. | 120
Details of cost for 100 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2862 | 32mm X 8mm bolts & nuts | each | 350 | 4 | 1400
= 2x(100/0.6) = 334 + 16 (Wastage @ 5%) = 350 Nos
2812 | 40 mm X 3 mm flat iron | kg | 22.06 | 37.8 | 833.87
= 84 x 0.24m = 20.16m @ 0.547kg/m = 11.03 kg
2855 | Steel fastener 6 mm X 75 mm | each | 336 | 5 | 1680
| Total cost of materials |  |  |  | 3913.87
| Cartage @ 1 % of A1 |  |  |  | 39.1387
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1005 | Fitter, Grade 2 | day | 0.5 | 407 | 203.5
1009 | Blacksmith, Grade 2 | day | 0.5 | 407 | 203.5
1010 | Mason, Grade 2 | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 13.5 | 368 | 4968
| TOTAL |  |  |  | 10425.5087
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1563.83
| Cost for 100 Metre |  |  |  | 11989.3387
| Rate per Metre |  |  |  | 119.8934
| Say |  |  |  | 120
120
Analysis of rate
7.8 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
7.8.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) |  |  | DSR Rate Rs. | 21
Details of cost for 100 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2881 | GI saddles 19mm x 0.55mm for conduit | each | 226 | 0.85 | 192.1
= 100/0.45 = 222 + 4 (Wastage @ 2%) = 226 Nos
2854 | Iron screws, 45 mm X 6 mm | each | 452 | 1 | 452
2935 | Cement, paint, sand etc. | L.S. | 2 | 4.5 | 9
| Total cost of materials |  |  |  | 653.1
| Cartage @ 1 % of A1 |  |  |  | 6.531
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 1842.631
| OVERHEADS & PROFIT @ 15 % |  |  |  | 276.39
| Cost for 100 Metre |  |  |  | 2119.021
| Rate per Metre |  |  |  | 21.1902
| Say |  |  |  | 21
21
Analysis of rate
7.8 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
7.8.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) |  |  | DSR Rate Rs. | 49
Details of cost for 100 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2862 | 32mm X 8mm bolts & nuts | each | 350 | 4 | 1400
= 2x(100/0.6) = 334 + 16 (Wastage @ 5%) = 350 Nos
2809 | 20/25 mm X 3 mm flat iron | kg | 9.06 | 37.8 | 342.47
= 84 x 0.16m = 13.44m @ 0.337kg/m = 4.53 kg
| Total cost of materials |  |  |  | 1742.47
| Cartage @ 1 % of A1 |  |  |  | 17.4247
LABOUR
1001 | Wireman | day | 1.25 | 447 | 558.75
1005 | Fitter, Grade 2 | day | 0.33 | 407 | 134.31
1009 | Blacksmith, Grade 2 | day | 0.33 | 407 | 134.31
1007 | Khallasi | day | 4.66 | 368 | 1714.88
| TOTAL |  |  |  | 4302.1447
| OVERHEADS & PROFIT @ 15 % |  |  |  | 645.32
| Cost for 100 Metre |  |  |  | 4947.4647
| Rate per Metre |  |  |  | 49.4746
| Say |  |  |  | 49
49
Analysis of rate
7.8 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
7.8.3 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) |  |  | DSR Rate Rs. | 61
Details of cost for 100 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2862 | 32mm X 8mm bolts & nuts | each | 350 | 4 | 1400
= 2x(100/0.6) = 334 + 16 (Wastage @ 5%) = 350 Nos
2809 | 20/25 mm X 3 mm flat iron | kg | 13.58 | 37.8 | 513.32
= 84 x 0.24m = 20.16m @ 0.337kg/m = 6.79 kg
| Total cost of materials |  |  |  | 1913.32
| Cartage @ 1 % of A1 |  |  |  | 19.1332
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1005 | Fitter, Grade 2 | day | 0.33 | 407 | 134.31
1009 | Blacksmith, Grade 2 | day | 0.33 | 407 | 134.31
1007 | Khallasi | day | 6.66 | 368 | 2450.88
| TOTAL |  |  |  | 5322.4532
| OVERHEADS & PROFIT @ 15 % |  |  |  | 798.37
| Cost for 100 Metre |  |  |  | 6120.8232
| Rate per Metre |  |  |  | 61.2082
| Say |  |  |  | 61
61
Analysis of rate
7.8 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
7.8.4 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) |  |  | DSR Rate Rs. | 96
Details of cost for 100 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2862 | 32mm X 8mm bolts & nuts | each | 350 | 4 | 1400
= 2x(100/0.6) = 334 + 16 (Wastage @ 5%) = 350 Nos
2812 | 40 mm X 3 mm flat iron | kg | 22.06 | 37.8 | 833.87
= 84 x 0.24m = 20.16m @ 0.547kg/m = 11.03 kg
| Total cost of materials |  |  |  | 2233.87
| Cartage @ 1 % of A1 |  |  |  | 22.3387
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1005 | Fitter, Grade 2 | day | 0.5 | 407 | 203.5
1009 | Blacksmith, Grade 2 | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 13 | 368 | 4784
| TOTAL |  |  |  | 8341.2087
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1251.18
| Cost for 100 Metre |  |  |  | 9592.3887
| Rate per Metre |  |  |  | 95.9239
| Say |  |  |  | 96
96
Analysis of rate
7.9 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required.
|  |  |  | DSR Rate Rs. | 333
Details of cost for One each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1010 | Mason, Grade 2 | day | 0.12 | 407 | 48.84
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 93
| OVERHEADS & PROFIT @ 15 % |  |  |  | 13.95
| TOTAL |  |  |  | 106.95
14.4 | Excavation including refilling as required | cum | 0.22 | 318 | 69.96
14.7 | Cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) | cum | 0.03 | 5207 | 156.21
| TOTAL |  |  |  | 333.12
| Rate per Each |  |  |  | 333.12
| Say |  |  |  | 333
333
Analysis of rate
7.10 | Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required.
|  |  |  | DSR Rate Rs. | 269
Details of cost for One each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2926 | G.I. plate ( 10 cm X 10 cm X 5 mm ) | kg | 0.39 | 46 | 17.94
2806 | 35 mm X 35 mm X 5 mm angle iron | kg | 1.97 | 37.8 | 74.47
2868 | 16 mm X 40 mm bolts and nuts with washers | set | 2 | 6 | 12
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 108.41
| Cartage @ 1 % of A1 |  |  |  | 1.0841
LABOUR
1005 | Fitter, Grade 2 | day | 0.12 | 407 | 48.84
1006 | Painter | day | 0.077 | 407 | 31.34
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 233.8341
| OVERHEADS & PROFIT @ 15 % |  |  |  | 35.08
| TOTAL |  |  |  | 268.9141
| Rate per Each |  |  |  | 268.9141
| Say |  |  |  | 269
269
CHAPTER 8 – H V CABLE LAYING (Analysis of rate based on DAR)
Analysis of rate
8.1 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
8.1.1 | Upto 120 sq. mm |  |  | DSR Rate Rs. | 273
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 8.76 | 672 | 5886.72
| Total cost of materials |  |  |  | 8640.72
| Cartage @ 1 % of A1 |  |  |  | 86.4072
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 8 | 368 | 2944
| TOTAL |  |  |  | 12118.1272
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1817.72
| TOTAL |  |  |  | 13935.8472
14.4 | Excavation including refilling as required | cum | 42 | 318 | 13356
| Cost for 100 Meters |  |  |  | 27291.8472
| Rate per Meter |  |  |  | 272.9185
| Say |  |  |  | 273
273
Analysis of rate
8.1 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
8.1.2 | Above 120 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 298
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 8.76 | 672 | 5886.72
| Total cost of materials |  |  |  | 8640.72
| Cartage @ 1 % of A1 |  |  |  | 86.4072
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 14 | 368 | 5152
| TOTAL |  |  |  | 14326.1272
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2148.92
| TOTAL |  |  |  | 16475.0472
14.4 | Excavation including refilling as required | cum | 42 | 318 | 13356
| Cost for 100 Meters |  |  |  | 29831.0472
| Rate per Meter |  |  |  | 298.3105
| Say |  |  |  | 298
298
Analysis of rate
8.2 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
8.2.1 | Upto 120 sq. mm |  |  | DSR Rate Rs. | 186
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 5 | 672 | 3360
| Total cost of materials |  |  |  | 6114
| Cartage @ 1 % of A1 |  |  |  | 61.14
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 8 | 368 | 2944
| TOTAL |  |  |  | 9566.14
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1434.92
| TOTAL |  |  |  | 11001.06
14.4 | Excavation including refilling as required | cum | 24 | 318 | 7632
| Cost for 100 Meters |  |  |  | 18633.06
| Rate per Meter |  |  |  | 186.3306
| Say |  |  |  | 186
186
Analysis of rate
8.2 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
8.2.2 | Above 120 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 212
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 5 | 672 | 3360
| Total cost of materials |  |  |  | 6114
| Cartage @ 1 % of A1 |  |  |  | 61.14
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 14 | 368 | 5152
| TOTAL |  |  |  | 11774.14
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1766.12
| TOTAL |  |  |  | 13540.26
14.4 | Excavation including refilling as required | cum | 24 | 318 | 7632
| Cost for 100 Meters |  |  |  | 21172.26
| Rate per Meter |  |  |  | 211.7226
| Say |  |  |  | 212
212
Analysis of rate
8.3 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
8.3.1 | Upto 120 sq. mm |  |  | DSR Rate Rs. | 37
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 7 | 368 | 2576
| TOTAL |  |  |  | 3246.5
| OVERHEADS & PROFIT @ 15 % |  |  |  | 486.98
| Cost for 100 Meters |  |  |  | 3733.48
| Rate per Meter |  |  |  | 37.3348
| Say |  |  |  | 37
37
Analysis of rate
8.3 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
8.3.2 | Above 120 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 65
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1007 | Khallasi | day | 13 | 368 | 4784
| TOTAL |  |  |  | 5678
| OVERHEADS & PROFIT @ 15 % |  |  |  | 851.7
| Cost for 100 Meters |  |  |  | 6529.7
| Rate per Meter |  |  |  | 65.297
| Say |  |  |  | 65
65
Analysis of rate
8.4 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing masonry open duct as required.
8.4.1 | Upto 120 sq. mm |  |  | DSR Rate Rs. | 31
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 6 | 368 | 2208
| TOTAL |  |  |  | 2655
| OVERHEADS & PROFIT @ 15 % |  |  |  | 398.25
| Cost for 100 Meters |  |  |  | 3053.25
| Rate per Meter |  |  |  | 30.5325
| Say |  |  |  | 31
31
Analysis of rate
8.4 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing masonry open duct as required.
8.4.2 | Above 120 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 56
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1 | 447 | 447
1007 | Khallasi | day | 12 | 368 | 4416
| TOTAL |  |  |  | 4863
| OVERHEADS & PROFIT @ 15 % |  |  |  | 729.45
| Cost for 100 Meters |  |  |  | 5592.45
| Rate per Meter |  |  |  | 55.9245
| Say |  |  |  | 56
56
Analysis of rate
8.5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 33 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
8.5.1 | Upto 120 sq. mm |  |  | DSR Rate Rs. | 275
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 8.76 | 672 | 5886.72
| Total cost of materials |  |  |  | 8640.72
| Cartage @ 1 % of A1 |  |  |  | 86.4072
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 8 | 368 | 2944
| TOTAL |  |  |  | 12341.6272
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1851.24
| TOTAL |  |  |  | 14192.8672
14.4 | Excavation including refilling as required | cum | 42 | 318 | 13356
| Cost for 100 Meters |  |  |  | 27548.8672
| Rate per Meter |  |  |  | 275.4887
| Say |  |  |  | 275
275
Analysis of rate
8.5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 33 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
8.5.2 | Above 120 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 301
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 8.76 | 672 | 5886.72
| Total cost of materials |  |  |  | 8640.72
| Cartage @ 1 % of A1 |  |  |  | 86.4072
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 14 | 368 | 5152
| TOTAL |  |  |  | 14549.6272
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2182.44
| TOTAL |  |  |  | 16732.0672
14.4 | Excavation including refilling as required | cum | 42 | 318 | 13356
| Cost for 100 Meters |  |  |  | 30088.0672
| Rate per Meter |  |  |  | 300.8807
| Say |  |  |  | 301
301
Analysis of rate
8.6 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 33 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
8.6.1 | Upto 120 sq. mm |  |  | DSR Rate Rs. | 189
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 5 | 672 | 3360
| Total cost of materials |  |  |  | 6114
| Cartage @ 1 % of A1 |  |  |  | 61.14
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 8 | 368 | 2944
| TOTAL |  |  |  | 9789.64
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1468.45
| TOTAL |  |  |  | 11258.09
14.4 | Excavation including refilling as required | cum | 24 | 318 | 7632
| Cost for 100 Meters |  |  |  | 18890.09
| Rate per Meter |  |  |  | 188.9009
| Say |  |  |  | 189
189
Analysis of rate
8.6 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 33 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
8.6.2 | Above 120 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 214
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 918 | 3 | 2754
= 874 + 44 (Wastage@ 5%) = 918 Nos
2946 | Fine sand | cum | 5 | 672 | 3360
| Total cost of materials |  |  |  | 6114
| Cartage @ 1 % of A1 |  |  |  | 61.14
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 14 | 368 | 5152
| TOTAL |  |  |  | 11997.64
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1799.65
| TOTAL |  |  |  | 13797.29
14.4 | Excavation including refilling as required | cum | 24 | 318 | 7632
| Cost for 100 Meters |  |  |  | 21429.29
| Rate per Meter |  |  |  | 214.2929
| Say |  |  |  | 214
214
Analysis of rate
8.7 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 33 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
8.7.1 | Upto 120 sq. mm |  |  | DSR Rate Rs. | 40
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 2 | 447 | 894
1007 | Khallasi | day | 7 | 368 | 2576
| TOTAL |  |  |  | 3470
| OVERHEADS & PROFIT @ 15 % |  |  |  | 520.5
| Cost for 100 Meters |  |  |  | 3990.5
| Rate per Meter |  |  |  | 39.905
| Say |  |  |  | 40
40
Analysis of rate
8.7 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 33 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
8.7.2 | Above 120 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 68
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 2.5 | 447 | 1117.5
1007 | Khallasi | day | 13 | 368 | 4784
| TOTAL |  |  |  | 5901.5
| OVERHEADS & PROFIT @ 15 % |  |  |  | 885.23
| Cost for 100 Meters |  |  |  | 6786.73
| Rate per Meter |  |  |  | 67.8673
| Say |  |  |  | 68
68
Analysis of rate
8.8 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 33 KV grade of following size in the existing masonry open duct as required.
8.8.1 | Upto 120 sq. mm |  |  | DSR Rate Rs. | 33
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 6 | 368 | 2208
| TOTAL |  |  |  | 2878.5
| OVERHEADS & PROFIT @ 15 % |  |  |  | 431.78
| Cost for 100 Meters |  |  |  | 3310.28
| Rate per Meter |  |  |  | 33.1028
| Say |  |  |  | 33
33
Analysis of rate
8.8 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 33 KV grade of following size in the existing masonry open duct as required.
8.8.2 | Above 120 sq. mm and upto 400 sq. mm |  |  | DSR Rate Rs. | 58
Details of cost for 100 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1001 | Wireman | day | 1.5 | 447 | 670.5
1007 | Khallasi | day | 12 | 368 | 4416
| TOTAL |  |  |  | 5086.5
| OVERHEADS & PROFIT @ 15 % |  |  |  | 762.98
| Cost for 100 Meters |  |  |  | 5849.48
| Rate per Meter |  |  |  | 58.4948
| Say |  |  |  | 58
58
CHAPTER 9 – MV CABLE JOINTING & END TERMINATION (Analysis of rate based on DAR)
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.1 | 2 X 6 sq. mm (19mm) |  |  | DSR Rate Rs. | 157
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2101 | Brass compression gland (19 mm) for 2 X 6 sq. mm 1.1 KV grade cable | set | 1 | 51.19 | 51.19
2201 | Aluminium lugs for 6 sq. mm cable | each | 2 | 1.59 | 3.18
| Total cost of materials |  |  |  | 54.37
| Cartage @ 1 % of A1 |  |  |  | 0.5437
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 136.4137
| OVERHEADS & PROFIT @ 15 % |  |  |  | 20.46
| TOTAL |  |  |  | 156.8737
| Rate per Set |  |  |  | 156.8737
| Say |  |  |  | 157
157
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.2 | 2 X 10 sq. mm (19mm) |  |  | DSR Rate Rs. | 158
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2102 | Brass compression gland (19 mm) for 2 X 10 sq. mm 1.1 KV grade cable | set | 1 | 51.19 | 51.19
2202 | Aluminium lugs for 10 sq. mm cable | each | 2 | 2.06 | 4.12
| Total cost of materials |  |  |  | 55.31
| Cartage @ 1 % of A1 |  |  |  | 0.5531
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 137.3631
| OVERHEADS & PROFIT @ 15 % |  |  |  | 20.6
| TOTAL |  |  |  | 157.9631
| Rate per Set |  |  |  | 157.9631
| Say |  |  |  | 158
158
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.3 | 2 X 16 sq. mm (22mm) |  |  | DSR Rate Rs. | 170
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2103 | Brass compression gland for (22 mm) 2 X 16 sq. mm 1.1 KV grade cable | set | 1 | 60.43 | 60.43
2203 | Aluminium lugs for 16 sq. mm cable | each | 2 | 2.47 | 4.94
| Total cost of materials |  |  |  | 65.37
| Cartage @ 1 % of A1 |  |  |  | 0.6537
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 147.5237
| OVERHEADS & PROFIT @ 15 % |  |  |  | 22.13
| TOTAL |  |  |  | 169.6537
| Rate per Set |  |  |  | 169.6537
| Say |  |  |  | 170
170
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.4 | 2 X 25 sq. mm (22mm) |  |  | DSR Rate Rs. | 171
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2104 | Brass compression gland for (22 mm) 2 X 25 sq. mm 1.1 KV grade cable | set | 1 | 60.43 | 60.43
2204 | Aluminium lugs for 25 sq. mm cable | each | 2 | 3.1 | 6.2
| Total cost of materials |  |  |  | 66.63
| Cartage @ 1 % of A1 |  |  |  | 0.6663
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 148.7963
| OVERHEADS & PROFIT @ 15 % |  |  |  | 22.32
| TOTAL |  |  |  | 171.1163
| Rate per Set |  |  |  | 171.1163
| Say |  |  |  | 171
171
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.5 | 2 X 35 sq. mm (25mm) |  |  | DSR Rate Rs. | 222
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2105 | Brass compression gland for (25 mm) 2 X 35 sq. mm 1.1 KV grade cable | set | 1 | 86.21 | 86.21
2205 | Aluminium lugs for 35 sq. mm cable | each | 2 | 4.1 | 8.2
| Total cost of materials |  |  |  | 94.41
| Cartage @ 1 % of A1 |  |  |  | 0.9441
LABOUR
1002 | Cable jointer | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 193.1541
| OVERHEADS & PROFIT @ 15 % |  |  |  | 28.97
| TOTAL |  |  |  | 222.1241
| Rate per Set |  |  |  | 222.1241
| Say |  |  |  | 222
222
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.6 | 2 X 50 sq. mm (28mm) |  |  | DSR Rate Rs. | 276
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2106 | Brass compression gland for (28 mm) 2 X 50 sq. mm 1.1 KV grade cable | set | 1 | 128.68 | 128.68
2206 | Aluminium lugs for 50 sq. mm cable | each | 2 | 6.21 | 12.42
| Total cost of materials |  |  |  | 141.1
| Cartage @ 1 % of A1 |  |  |  | 1.411
LABOUR
1002 | Cable jointer | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 240.311
| OVERHEADS & PROFIT @ 15 % |  |  |  | 36.05
| TOTAL |  |  |  | 276.361
| Rate per Set |  |  |  | 276.361
| Say |  |  |  | 276
276
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.7 | 3 X 10 sq. mm (22mm) |  |  | DSR Rate Rs. | 171
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2107 | Brass compression gland for (22 mm) 3 X 10 sq. mm 1.1 KV grade cable | set | 1 | 60.43 | 60.43
2202 | Aluminium lugs for 10 sq. mm cable | each | 3 | 2.06 | 6.18
| Total cost of materials |  |  |  | 66.61
| Cartage @ 1 % of A1 |  |  |  | 0.6661
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 148.7761
| OVERHEADS & PROFIT @ 15 % |  |  |  | 22.32
| TOTAL |  |  |  | 171.0961
| Rate per Set |  |  |  | 171.0961
| Say |  |  |  | 171
171
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.8 | 3 X 16 sq. mm (25mm) |  |  | DSR Rate Rs. | 202
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2108 | Brass compression gland for (25 mm) 3 X 16 sq. mm 1.1 KV grade cable | set | 1 | 86.21 | 86.21
2203 | Aluminium lugs for 16 sq. mm cable | each | 3 | 2.47 | 7.41
| Total cost of materials |  |  |  | 93.62
| Cartage @ 1 % of A1 |  |  |  | 0.9362
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 176.0562
| OVERHEADS & PROFIT @ 15 % |  |  |  | 26.41
| TOTAL |  |  |  | 202.4662
| Rate per Set |  |  |  | 202.4662
| Say |  |  |  | 202
202
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.9 | 3 X 25 sq. mm (25mm) |  |  | DSR Rate Rs. | 205
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2109 | Brass compression gland for (25 mm) 3 X 25 sq. mm 1.1 KV grade cable | set | 1 | 86.21 | 86.21
2204 | Aluminium lugs for 25 sq. mm cable | each | 3 | 3.1 | 9.3
| Total cost of materials |  |  |  | 95.51
| Cartage @ 1 % of A1 |  |  |  | 0.9551
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 177.9651
| OVERHEADS & PROFIT @ 15 % |  |  |  | 26.69
| TOTAL |  |  |  | 204.6551
| Rate per Set |  |  |  | 204.6551
| Say |  |  |  | 205
205
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.10 | 3 X 35 sq. mm (28mm) |  |  | DSR Rate Rs. | 276
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2110 | Brass compression gland for (28 mm) 3 X 35 sq. mm 1.1 KV grade cable | set | 1 | 128.68 | 128.68
2205 | Aluminium lugs for 35 sq. mm cable | each | 3 | 4.1 | 12.3
| Total cost of materials |  |  |  | 140.98
| Cartage @ 1 % of A1 |  |  |  | 1.4098
LABOUR
1002 | Cable jointer | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 240.1898
| OVERHEADS & PROFIT @ 15 % |  |  |  | 36.03
| TOTAL |  |  |  | 276.2198
| Rate per Set |  |  |  | 276.2198
| Say |  |  |  | 276
276
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.11 | 3 X 50 sq. mm (32mm) |  |  | DSR Rate Rs. | 286
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2111 | Brass compression gland for (32 mm) 3 X 50 sq. mm 1.1 KV grade cable | set | 1 | 130.62 | 130.62
2206 | Aluminium lugs for 50 sq. mm cable | each | 3 | 6.21 | 18.63
| Total cost of materials |  |  |  | 149.25
| Cartage @ 1 % of A1 |  |  |  | 1.4925
LABOUR
1002 | Cable jointer | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 248.5425
| OVERHEADS & PROFIT @ 15 % |  |  |  | 37.28
| TOTAL |  |  |  | 285.8225
| Rate per Set |  |  |  | 285.8225
| Say |  |  |  | 286
286
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.12 | 3 X 70 sq. mm (35mm) |  |  | DSR Rate Rs. | 361
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2112 | Brass compression gland for (35 mm) 3 X 70 sq. mm 1.1 KV grade cable | set | 1 | 186.27 | 186.27
2207 | Aluminium lugs for 70 sq. mm cable | each | 3 | 9.3 | 27.9
| Total cost of materials |  |  |  | 214.17
| Cartage @ 1 % of A1 |  |  |  | 2.1417
LABOUR
1002 | Cable jointer | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 314.1117
| OVERHEADS & PROFIT @ 15 % |  |  |  | 47.12
| TOTAL |  |  |  | 361.2317
| Rate per Set |  |  |  | 361.2317
| Say |  |  |  | 361
361
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.13 | 3 X 95 sq. mm (38mm) |  |  | DSR Rate Rs. | 431
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2113 | Brass compression gland for (38 mm) 3 X 95 sq. mm 1.1 KV grade cable | set | 1 | 210.79 | 210.79
2208 | Aluminium lugs for 95 sq. mm cable | each | 3 | 10.27 | 30.81
| Total cost of materials |  |  |  | 241.6
| Cartage @ 1 % of A1 |  |  |  | 2.416
LABOUR
1002 | Cable jointer | day | 0.16 | 447 | 71.52
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 374.416
| OVERHEADS & PROFIT @ 15 % |  |  |  | 56.16
| TOTAL |  |  |  | 430.576
| Rate per Set |  |  |  | 430.576
| Say |  |  |  | 431
431
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.14 | 3 X 120 sq. mm (45mm) |  |  | DSR Rate Rs. | 489
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2114 | Brass compression gland for (45 mm) 3 X 120 sq. mm 1.1 KV grade cable | set | 1 | 248.9 | 248.9
2209 | Aluminium lugs for 120 sq. mm cable | each | 3 | 14.38 | 43.14
| Total cost of materials |  |  |  | 292.04
| Cartage @ 1 % of A1 |  |  |  | 2.9204
LABOUR
1002 | Cable jointer | day | 0.16 | 447 | 71.52
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 425.3604
| OVERHEADS & PROFIT @ 15 % |  |  |  | 63.8
| TOTAL |  |  |  | 489.1604
| Rate per Set |  |  |  | 489.1604
| Say |  |  |  | 489
489
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.15 | 3 X 150 sq. mm (50mm) |  |  | DSR Rate Rs. | 580
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2115 | Brass compression gland for (50 mm) 3 X 150 sq. mm 1.1 KV grade cable | set | 1 | 314.74 | 314.74
2210 | Aluminium lugs for 150 sq. mm cable | each | 3 | 18.61 | 55.83
| Total cost of materials |  |  |  | 370.57
| Cartage @ 1 % of A1 |  |  |  | 3.7057
LABOUR
1002 | Cable jointer | day | 0.16 | 447 | 71.52
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 504.6757
| OVERHEADS & PROFIT @ 15 % |  |  |  | 75.7
| TOTAL |  |  |  | 580.3757
| Rate per Set |  |  |  | 580.3757
| Say |  |  |  | 580
580
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.16 | 3 X 185 sq. mm (57mm) |  |  | DSR Rate Rs. | 792
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2116 | Brass compression gland for (57 mm) 3 X 185 sq. mm 1.1 KV grade cable | set | 1 | 450.45 | 450.45
2211 | Aluminium lugs for 185 sq. mm cable | each | 3 | 23.27 | 69.81
| Total cost of materials |  |  |  | 520.26
| Cartage @ 1 % of A1 |  |  |  | 5.2026
LABOUR
1002 | Cable jointer | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 688.4626
| OVERHEADS & PROFIT @ 15 % |  |  |  | 103.27
| TOTAL |  |  |  | 791.7326
| Rate per Set |  |  |  | 791.7326
| Say |  |  |  | 792
792
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.17 | 3 X 225 sq. mm (62mm) |  |  | DSR Rate Rs. | 947
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2117 | Brass compression gland for (62 mm) 3 X 225 sq. mm 1.1 KV grade cable | set | 1 | 556.71 | 556.71
2212 | Aluminium lugs for 225 sq. mm cable | each | 3 | 32.55 | 97.65
| Total cost of materials |  |  |  | 654.36
| Cartage @ 1 % of A1 |  |  |  | 6.5436
LABOUR
1002 | Cable jointer | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 823.9036
| OVERHEADS & PROFIT @ 15 % |  |  |  | 123.59
| TOTAL |  |  |  | 947.4936
| Rate per Set |  |  |  | 947.4936
| Say |  |  |  | 947
947
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.18 | 3 X 240 sq. mm (62mm) |  |  | DSR Rate Rs. | 973
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2118 | Brass compression gland for (62 mm) 3 X 240 sq. mm 1.1 KV grade cable | set | 1 | 556.71 | 556.71
2213 | Aluminium lugs for 240 sq. mm cable | each | 3 | 39.75 | 119.25
| Total cost of materials |  |  |  | 675.96
| Cartage @ 1 % of A1 |  |  |  | 6.7596
LABOUR
1002 | Cable jointer | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 845.7196
| OVERHEADS & PROFIT @ 15 % |  |  |  | 126.86
| TOTAL |  |  |  | 972.5796
| Rate per Set |  |  |  | 972.5796
| Say |  |  |  | 973
973
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.19 | 3 X 300 sq. mm (70mm) |  |  | DSR Rate Rs. | 1084
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2119 | Brass compression gland for (70 mm) 3 X 300 sq. mm 1.1 KV grade cable | set | 1 | 604.38 | 604.38
2214 | Aluminium lugs for 300 sq. mm cable | each | 3 | 55.83 | 167.49
| Total cost of materials |  |  |  | 771.87
| Cartage @ 1 % of A1 |  |  |  | 7.7187
LABOUR
1002 | Cable jointer | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 942.5887
| OVERHEADS & PROFIT @ 15 % |  |  |  | 141.39
| TOTAL |  |  |  | 1083.9787
| Rate per Set |  |  |  | 1083.9787
| Say |  |  |  | 1084
1084
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.20 | 3½ X 25 sq. mm (28mm) |  |  | DSR Rate Rs. | 257
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2120 | Brass compression gland for (28 mm) 3½ X 25 sq. mm 1.1 KV grade cable | set | 1 | 128.68 | 128.68
2204 | Aluminium lugs for 25 sq. mm cable | each | 3 | 3.1 | 9.3
2203 | Aluminium lugs for 16 sq. mm cable | each | 1 | 2.47 | 2.47
| Total cost of materials |  |  |  | 140.45
| Cartage @ 1 % of A1 |  |  |  | 1.4045
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 223.3545
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.5
| TOTAL |  |  |  | 256.8545
| Rate per Set |  |  |  | 256.8545
| Say |  |  |  | 257
257
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.21 | 3½ X 35 sq. mm (32mm) |  |  | DSR Rate Rs. | 282
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2121 | Brass compression gland for (32 mm) 3½ X 35 sq. mm 1.1 KV grade cable | set | 1 | 130.62 | 130.62
2205 | Aluminium lugs for 35 sq. mm cable | each | 3 | 4.1 | 12.3
2204 | Aluminium lugs for 25 sq. mm cable | each | 1 | 3.1 | 3.1
| Total cost of materials |  |  |  | 146.02
| Cartage @ 1 % of A1 |  |  |  | 1.4602
LABOUR
1002 | Cable jointer | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 245.2802
| OVERHEADS & PROFIT @ 15 % |  |  |  | 36.79
| TOTAL |  |  |  | 282.0702
| Rate per Set |  |  |  | 282.0702
| Say |  |  |  | 282
282
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.22 | 3½ X 50 sq. mm (35mm) |  |  | DSR Rate Rs. | 354
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2122 | Brass compression gland for (35 mm) 3½ X 50 sq. mm 1.1 KV grade cable | set | 1 | 186.27 | 186.27
2206 | Aluminium lugs for 50 sq. mm cable | each | 3 | 6.21 | 18.63
2204 | Aluminium lugs for 25 sq. mm cable | each | 1 | 3.1 | 3.1
| Total cost of materials |  |  |  | 208
| Cartage @ 1 % of A1 |  |  |  | 2.08
LABOUR
1002 | Cable jointer | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 307.88
| OVERHEADS & PROFIT @ 15 % |  |  |  | 46.18
| TOTAL |  |  |  | 354.06
| Rate per Set |  |  |  | 354.06
| Say |  |  |  | 354
354
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.23 | 3½ X 70 sq. mm (38mm) |  |  | DSR Rate Rs. | 394
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2123 | Brass compression gland for (38 mm) 3½ X 70 sq. mm 1.1 KV grade cable | set | 1 | 210.79 | 210.79
2207 | Aluminium lugs for 70 sq. mm cable | each | 3 | 9.3 | 27.9
2205 | Aluminium lugs for 35 sq. mm cable | each | 1 | 4.1 | 4.1
| Total cost of materials |  |  |  | 242.79
| Cartage @ 1 % of A1 |  |  |  | 2.4279
LABOUR
1002 | Cable jointer | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 343.0179
| OVERHEADS & PROFIT @ 15 % |  |  |  | 51.45
| TOTAL |  |  |  | 394.4679
| Rate per Set |  |  |  | 394.4679
| Say |  |  |  | 394
394
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.24 | 3½ X 95 sq. mm (45mm) |  |  | DSR Rate Rs. | 482
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2124 | Brass compression gland for (45 mm) 3½ X 95 sq. mm 1.1 KV grade cable | set | 1 | 248.9 | 248.9
2208 | Aluminium lugs for 95 sq. mm cable | each | 3 | 10.27 | 30.81
2206 | Aluminium lugs for 50 sq. mm cable | each | 1 | 6.21 | 6.21
| Total cost of materials |  |  |  | 285.92
| Cartage @ 1 % of A1 |  |  |  | 2.8592
LABOUR
1002 | Cable jointer | day | 0.16 | 447 | 71.52
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 419.1792
| OVERHEADS & PROFIT @ 15 % |  |  |  | 62.88
| TOTAL |  |  |  | 482.0592
| Rate per Set |  |  |  | 482.0592
| Say |  |  |  | 482
482
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.25 | 3½ X 120 sq. mm (45mm) |  |  | DSR Rate Rs. | 500
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2125 | Brass compression gland for (45 mm) 3½ X 120 sq. mm 1.1 KV grade cable | set | 1 | 248.9 | 248.9
2209 | Aluminium lugs for 120 sq. mm cable | each | 3 | 14.38 | 43.14
2207 | Aluminium lugs for 70 sq. mm cable | each | 1 | 9.3 | 9.3
| Total cost of materials |  |  |  | 301.34
| Cartage @ 1 % of A1 |  |  |  | 3.0134
LABOUR
1002 | Cable jointer | day | 0.16 | 447 | 71.52
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 434.7534
| OVERHEADS & PROFIT @ 15 % |  |  |  | 65.21
| TOTAL |  |  |  | 499.9634
| Rate per Set |  |  |  | 499.9634
| Say |  |  |  | 500
500
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.26 | 3½ X 150 sq. mm (50mm) |  |  | DSR Rate Rs. | 592
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2126 | Brass compression gland for (50 mm) 3½ X 150 sq. mm 1.1 KV grade cable | set | 1 | 314.74 | 314.74
2210 | Aluminium lugs for 150 sq. mm cable | each | 3 | 18.61 | 55.83
2208 | Aluminium lugs for 95 sq. mm cable | each | 1 | 10.27 | 10.27
| Total cost of materials |  |  |  | 380.84
| Cartage @ 1 % of A1 |  |  |  | 3.8084
LABOUR
1002 | Cable jointer | day | 0.16 | 447 | 71.52
1007 | Khallasi | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 515.0484
| OVERHEADS & PROFIT @ 15 % |  |  |  | 77.26
| TOTAL |  |  |  | 592.3084
| Rate per Set |  |  |  | 592.3084
| Say |  |  |  | 592
592
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.27 | 3½ X 185 sq. mm (57mm) |  |  | DSR Rate Rs. | 804
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2127 | Brass compression gland for (57 mm) 3½ X 185 sq. mm 1.1 KV grade cable | set | 1 | 450.45 | 450.45
2211 | Aluminium lugs for 185 sq. mm cable | each | 3 | 23.27 | 69.81
2208 | Aluminium lugs for 95 sq. mm cable | each | 1 | 10.27 | 10.27
| Total cost of materials |  |  |  | 530.53
| Cartage @ 1 % of A1 |  |  |  | 5.3053
LABOUR
1002 | Cable jointer | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 698.8353
| OVERHEADS & PROFIT @ 15 % |  |  |  | 104.83
| TOTAL |  |  |  | 803.6653
| Rate per Set |  |  |  | 803.6653
| Say |  |  |  | 804
804
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.28 | 3½ X 225 sq. mm (62mm) |  |  | DSR Rate Rs. | 964
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2128 | Brass compression gland for (62 mm) 3½ X 225 sq. mm 1.1 KV grade cable | set | 1 | 556.71 | 556.71
2212 | Aluminium lugs for 225 sq. mm cable | each | 3 | 32.55 | 97.65
2209 | Aluminium lugs for 120 sq. mm cable | each | 1 | 14.38 | 14.38
| Total cost of materials |  |  |  | 668.74
| Cartage @ 1 % of A1 |  |  |  | 6.6874
LABOUR
1002 | Cable jointer | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 838.4274
| OVERHEADS & PROFIT @ 15 % |  |  |  | 125.76
| TOTAL |  |  |  | 964.1874
| Rate per Set |  |  |  | 964.1874
| Say |  |  |  | 964
964
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.29 | 3½ X 240 sq. mm (62mm) |  |  | DSR Rate Rs. | 989
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2129 | Brass compression gland for (62 mm) 3½ X 240 sq. mm 1.1 KV grade cable | set | 1 | 556.71 | 556.71
2213 | Aluminium lugs for 240 sq. mm cable | each | 3 | 39.75 | 119.25
2209 | Aluminium lugs for 120 sq. mm cable | each | 1 | 14.38 | 14.38
| Total cost of materials |  |  |  | 690.34
| Cartage @ 1 % of A1 |  |  |  | 6.9034
LABOUR
1002 | Cable jointer | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 860.2434
| OVERHEADS & PROFIT @ 15 % |  |  |  | 129.04
| TOTAL |  |  |  | 989.2834
| Rate per Set |  |  |  | 989.2834
| Say |  |  |  | 989
989
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.30 | 3½ X 300 sq. mm (70mm) |  |  | DSR Rate Rs. | 1106
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2130 | Brass compression gland for (70 mm) 3½ X 300 sq. mm 1.1 KV grade cable | set | 1 | 604.38 | 604.38
2214 | Aluminium lugs for 300 sq. mm cable | each | 3 | 55.83 | 167.49
2210 | Aluminium lugs for 150 sq. mm cable | each | 1 | 18.61 | 18.61
| Total cost of materials |  |  |  | 790.48
| Cartage @ 1 % of A1 |  |  |  | 7.9048
LABOUR
1002 | Cable jointer | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 961.3848
| OVERHEADS & PROFIT @ 15 % |  |  |  | 144.21
| TOTAL |  |  |  | 1105.5948
| Rate per Set |  |  |  | 1105.5948
| Say |  |  |  | 1106
1106
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.31 | 3½ X 400 sq. mm (82mm) |  |  | DSR Rate Rs. | 1389
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2131 | Brass compression gland for (82 mm) 3½ X 400 sq. mm 1.1 KV grade cable | set | 1 | 760.31 | 760.31
2215 | Aluminium lugs for 400 sq. mm cable | each | 3 | 80.68 | 242.04
2212 | Aluminium lugs for 225 sq. mm cable | each | 1 | 32.55 | 32.55
| Total cost of materials |  |  |  | 1034.9
| Cartage @ 1 % of A1 |  |  |  | 10.349
LABOUR
1002 | Cable jointer | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 1208.249
| OVERHEADS & PROFIT @ 15 % |  |  |  | 181.24
| TOTAL |  |  |  | 1389.489
| Rate per Set |  |  |  | 1389.489
| Say |  |  |  | 1389
1389
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.32 | 4 X 10 sq. mm (25mm) |  |  | DSR Rate Rs. | 203
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2132 | Brass compression gland for (25 mm) 4 X 10 sq. mm 1.1 KV grade cable | set | 1 | 86.21 | 86.21
2202 | Aluminium lugs for 10 sq. mm cable | each | 4 | 2.06 | 8.24
| Total cost of materials |  |  |  | 94.45
| Cartage @ 1 % of A1 |  |  |  | 0.9445
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 176.8945
| OVERHEADS & PROFIT @ 15 % |  |  |  | 26.53
| TOTAL |  |  |  | 203.4245
| Rate per Set |  |  |  | 203.4245
| Say |  |  |  | 203
203
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.33 | 4 X 16 sq. mm (28mm) |  |  | DSR Rate Rs. | 255
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2133 | Brass compression gland for (28 mm) 4 X 16 sq. mm 1.1 KV grade cable | set | 1 | 128.68 | 128.68
2203 | Aluminium lugs for 16 sq. mm cable | each | 4 | 2.47 | 9.88
| Total cost of materials |  |  |  | 138.56
| Cartage @ 1 % of A1 |  |  |  | 1.3856
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 221.4456
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.22
| TOTAL |  |  |  | 254.6656
| Rate per Set |  |  |  | 254.6656
| Say |  |  |  | 255
255
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.34 | 4 X 25 sq. mm (28mm) |  |  | DSR Rate Rs. | 258
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2134 | Brass compression gland for (28 mm) 4 X 25 sq. mm 1.1 KV grade cable | set | 1 | 128.68 | 128.68
2204 | Aluminium lugs for 25 sq. mm cable | each | 4 | 3.1 | 12.4
| Total cost of materials |  |  |  | 141.08
| Cartage @ 1 % of A1 |  |  |  | 1.4108
LABOUR
1002 | Cable jointer | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 223.9908
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33.6
| TOTAL |  |  |  | 257.5908
| Rate per Set |  |  |  | 257.5908
| Say |  |  |  | 258
258
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.35 | 4 X 35 sq. mm (32mm) |  |  | DSR Rate Rs. | 283
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2135 | Brass compression gland for (32 mm) 4 X 35 sq. mm 1.1 KV grade cable | set | 1 | 130.62 | 130.62
2205 | Aluminium lugs for 35 sq. mm cable | each | 4 | 4.1 | 16.4
| Total cost of materials |  |  |  | 147.02
| Cartage @ 1 % of A1 |  |  |  | 1.4702
LABOUR
1002 | Cable jointer | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 246.2902
| OVERHEADS & PROFIT @ 15 % |  |  |  | 36.94
| TOTAL |  |  |  | 283.2302
| Rate per Set |  |  |  | 283.2302
| Say |  |  |  | 283
283
Analysis of rate
9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.36 | 4 X 50 sq. mm (35mm) |  |  | DSR Rate Rs. | 358
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2136 | Brass compression gland for (35 mm) 4 X 50 sq. mm 1.1 KV grade cable | set | 1 | 186.27 | 186.27
2206 | Aluminium lugs for 50 sq. mm cable | each | 4 | 6.21 | 24.84
| Total cost of materials |  |  |  | 211.11
| Cartage @ 1 % of A1 |  |  |  | 2.1111
LABOUR
1002 | Cable jointer | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 311.0211
| OVERHEADS & PROFIT @ 15 % |  |  |  | 46.65
| TOTAL |  |  |  | 357.6711
| Rate per Set |  |  |  | 357.6711
| Say |  |  |  | 358
358
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.1 | 2 X 16 sq. mm |  |  | DSR Rate Rs. | 617
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2300 | Outdoor cable jointing kit with cast resin compound with lugs for 2 X 16 sq. mm 1.1 KV grade cable | set | 1 | 329.18 | 329.18
| Total cost of materials |  |  |  | 329.18
| Cartage @ 1 % of A1 |  |  |  | 3.2918
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 536.2218
| OVERHEADS & PROFIT @ 15 % |  |  |  | 80.43
| TOTAL |  |  |  | 616.6518
| Rate per Set |  |  |  | 616.6518
| Say |  |  |  | 617
617
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.2 | 2 X 25 sq. mm |  |  | DSR Rate Rs. | 663
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2301 | Outdoor cable jointing kit with cast resin compound with lugs for 2 X 25 sq. mm 1.1 KV grade cable | set | 1 | 369.08 | 369.08
| Total cost of materials |  |  |  | 369.08
| Cartage @ 1 % of A1 |  |  |  | 3.6908
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 576.5208
| OVERHEADS & PROFIT @ 15 % |  |  |  | 86.48
| TOTAL |  |  |  | 663.0008
| Rate per Set |  |  |  | 663.0008
| Say |  |  |  | 663
663
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.3 | 2 X 35 sq. mm |  |  | DSR Rate Rs. | 663
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2302 | Outdoor cable jointing kit with cast resin compound with lugs for 2 X 35 sq. mm 1.1 KV grade cable | set | 1 | 369.08 | 369.08
| Total cost of materials |  |  |  | 369.08
| Cartage @ 1 % of A1 |  |  |  | 3.6908
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 576.5208
| OVERHEADS & PROFIT @ 15 % |  |  |  | 86.48
| TOTAL |  |  |  | 663.0008
| Rate per Set |  |  |  | 663.0008
| Say |  |  |  | 663
663
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.4 | 2 X 50 sq. mm |  |  | DSR Rate Rs. | 663
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2303 | Outdoor cable jointing kit with cast resin compound with lugs for 2 X 50 sq. mm 1.1 KV grade cable | set | 1 | 369.08 | 369.08
| Total cost of materials |  |  |  | 369.08
| Cartage @ 1 % of A1 |  |  |  | 3.6908
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 576.5208
| OVERHEADS & PROFIT @ 15 % |  |  |  | 86.48
| TOTAL |  |  |  | 663.0008
| Rate per Set |  |  |  | 663.0008
| Say |  |  |  | 663
663
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.5 | 3 X 16 sq. mm |  |  | DSR Rate Rs. | 663
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2304 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 16 sq. mm 1.1 KV grade cable | set | 1 | 369.08 | 369.08
| Total cost of materials |  |  |  | 369.08
| Cartage @ 1 % of A1 |  |  |  | 3.6908
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 576.5208
| OVERHEADS & PROFIT @ 15 % |  |  |  | 86.48
| TOTAL |  |  |  | 663.0008
| Rate per Set |  |  |  | 663.0008
| Say |  |  |  | 663
663
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.6 | 3 X 25 sq. mm |  |  | DSR Rate Rs. | 663
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2305 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 25 sq. mm 1.1 KV grade cable | set | 1 | 369.08 | 369.08
| Total cost of materials |  |  |  | 369.08
| Cartage @ 1 % of A1 |  |  |  | 3.6908
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 576.5208
| OVERHEADS & PROFIT @ 15 % |  |  |  | 86.48
| TOTAL |  |  |  | 663.0008
| Rate per Set |  |  |  | 663.0008
| Say |  |  |  | 663
663
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.7 | 3 X 35 sq. mm |  |  | DSR Rate Rs. | 663
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2306 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 35 sq. mm 1.1 KV grade cable | set | 1 | 369.08 | 369.08
| Total cost of materials |  |  |  | 369.08
| Cartage @ 1 % of A1 |  |  |  | 3.6908
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 576.5208
| OVERHEADS & PROFIT @ 15 % |  |  |  | 86.48
| TOTAL |  |  |  | 663.0008
| Rate per Set |  |  |  | 663.0008
| Say |  |  |  | 663
663
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.8 | 3 X 50 sq. mm |  |  | DSR Rate Rs. | 706
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2307 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 50 sq. mm 1.1 KV grade cable | set | 1 | 405.83 | 405.83
| Total cost of materials |  |  |  | 405.83
| Cartage @ 1 % of A1 |  |  |  | 4.0583
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 613.6383
| OVERHEADS & PROFIT @ 15 % |  |  |  | 92.05
| TOTAL |  |  |  | 705.6883
| Rate per Set |  |  |  | 705.6883
| Say |  |  |  | 706
706
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.9 | 3 X 70 sq. mm |  |  | DSR Rate Rs. | 706
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2308 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 70 sq. mm 1.1 KV grade cable | set | 1 | 405.83 | 405.83
| Total cost of materials |  |  |  | 405.83
| Cartage @ 1 % of A1 |  |  |  | 4.0583
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 613.6383
| OVERHEADS & PROFIT @ 15 % |  |  |  | 92.05
| TOTAL |  |  |  | 705.6883
| Rate per Set |  |  |  | 705.6883
| Say |  |  |  | 706
706
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.10 | 3 X 95 sq. mm |  |  | DSR Rate Rs. | 846
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2309 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 95 sq. mm 1.1 KV grade cable | set | 1 | 462 | 462
| Total cost of materials |  |  |  | 462
| Cartage @ 1 % of A1 |  |  |  | 4.62
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 735.57
| OVERHEADS & PROFIT @ 15 % |  |  |  | 110.34
| TOTAL |  |  |  | 845.91
| Rate per Set |  |  |  | 845.91
| Say |  |  |  | 846
846
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.11 | 3 X 120 sq. mm |  |  | DSR Rate Rs. | 846
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2310 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 120 sq. mm 1.1 KV grade cable | set | 1 | 462 | 462
| Total cost of materials |  |  |  | 462
| Cartage @ 1 % of A1 |  |  |  | 4.62
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 735.57
| OVERHEADS & PROFIT @ 15 % |  |  |  | 110.34
| TOTAL |  |  |  | 845.91
| Rate per Set |  |  |  | 845.91
| Say |  |  |  | 846
846
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.12 | 3 X 150 sq. mm |  |  | DSR Rate Rs. | 846
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2311 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 150 sq. mm 1.1 KV grade cable | set | 1 | 462 | 462
| Total cost of materials |  |  |  | 462
| Cartage @ 1 % of A1 |  |  |  | 4.62
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 735.57
| OVERHEADS & PROFIT @ 15 % |  |  |  | 110.34
| TOTAL |  |  |  | 845.91
| Rate per Set |  |  |  | 845.91
| Say |  |  |  | 846
846
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.13 | 3 X 185 sq. mm |  |  | DSR Rate Rs. | 1120
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2312 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 185 sq. mm 1.1 KV grade cable | set | 1 | 697.73 | 697.73
| Total cost of materials |  |  |  | 697.73
| Cartage @ 1 % of A1 |  |  |  | 6.9773
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 973.6573
| OVERHEADS & PROFIT @ 15 % |  |  |  | 146.05
| TOTAL |  |  |  | 1119.7073
| Rate per Set |  |  |  | 1119.7073
| Say |  |  |  | 1120
1120
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.14 | 3 X 225 sq. mm |  |  | DSR Rate Rs. | 1120
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2313 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 225 sq. mm 1.1 KV grade cable | set | 1 | 697.73 | 697.73
| Total cost of materials |  |  |  | 697.73
| Cartage @ 1 % of A1 |  |  |  | 6.9773
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 973.6573
| OVERHEADS & PROFIT @ 15 % |  |  |  | 146.05
| TOTAL |  |  |  | 1119.7073
| Rate per Set |  |  |  | 1119.7073
| Say |  |  |  | 1120
1120
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.15 | 3 X 240 sq. mm |  |  | DSR Rate Rs. | 1290
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2314 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 240 sq. mm 1.1 KV grade cable | set | 1 | 844.2 | 844.2
| Total cost of materials |  |  |  | 844.2
| Cartage @ 1 % of A1 |  |  |  | 8.442
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1121.592
| OVERHEADS & PROFIT @ 15 % |  |  |  | 168.24
| TOTAL |  |  |  | 1289.832
| Rate per Set |  |  |  | 1289.832
| Say |  |  |  | 1290
1290
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.16 | 3 X 300 sq. mm |  |  | DSR Rate Rs. | 1290
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2315 | Outdoor cable jointing kit with cast resin compound with lugs for 3 X 300 sq. mm 1.1 KV grade cable | set | 1 | 844.2 | 844.2
| Total cost of materials |  |  |  | 844.2
| Cartage @ 1 % of A1 |  |  |  | 8.442
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1121.592
| OVERHEADS & PROFIT @ 15 % |  |  |  | 168.24
| TOTAL |  |  |  | 1289.832
| Rate per Set |  |  |  | 1289.832
| Say |  |  |  | 1290
1290
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.17 | 3½ X 25 sq. mm |  |  | DSR Rate Rs. | 663
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2316 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 25 sq. mm 1.1 KV grade cable | set | 1 | 369.08 | 369.08
| Total cost of materials |  |  |  | 369.08
| Cartage @ 1 % of A1 |  |  |  | 3.6908
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 576.5208
| OVERHEADS & PROFIT @ 15 % |  |  |  | 86.48
| TOTAL |  |  |  | 663.0008
| Rate per Set |  |  |  | 663.0008
| Say |  |  |  | 663
663
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.18 | 3½ X 35 sq. mm |  |  | DSR Rate Rs. | 706
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2317 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 35 sq. mm 1.1 KV grade cable | set | 1 | 405.83 | 405.83
| Total cost of materials |  |  |  | 405.83
| Cartage @ 1 % of A1 |  |  |  | 4.0583
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 613.6383
| OVERHEADS & PROFIT @ 15 % |  |  |  | 92.05
| TOTAL |  |  |  | 705.6883
| Rate per Set |  |  |  | 705.6883
| Say |  |  |  | 706
706
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.19 | 3½ X 50 sq. mm |  |  | DSR Rate Rs. | 706
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2318 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 50 sq. mm 1.1 KV grade cable | set | 1 | 405.83 | 405.83
| Total cost of materials |  |  |  | 405.83
| Cartage @ 1 % of A1 |  |  |  | 4.0583
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 613.6383
| OVERHEADS & PROFIT @ 15 % |  |  |  | 92.05
| TOTAL |  |  |  | 705.6883
| Rate per Set |  |  |  | 705.6883
| Say |  |  |  | 706
706
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.20 | 3½ X 70 sq. mm |  |  | DSR Rate Rs. | 771
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2319 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 70 sq. mm 1.1 KV grade cable | set | 1 | 462 | 462
| Total cost of materials |  |  |  | 462
| Cartage @ 1 % of A1 |  |  |  | 4.62
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 670.37
| OVERHEADS & PROFIT @ 15 % |  |  |  | 100.56
| TOTAL |  |  |  | 770.93
| Rate per Set |  |  |  | 770.93
| Say |  |  |  | 771
771
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.21 | 3½ X 95 sq. mm |  |  | DSR Rate Rs. | 846
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2320 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 95 sq. mm 1.1 KV grade cable | set | 1 | 462 | 462
| Total cost of materials |  |  |  | 462
| Cartage @ 1 % of A1 |  |  |  | 4.62
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 735.57
| OVERHEADS & PROFIT @ 15 % |  |  |  | 110.34
| TOTAL |  |  |  | 845.91
| Rate per Set |  |  |  | 845.91
| Say |  |  |  | 846
846
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.22 | 3½ X 120 sq. mm |  |  | DSR Rate Rs. | 846
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2321 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 120 sq. mm 1.1 KV grade cable | set | 1 | 462 | 462
| Total cost of materials |  |  |  | 462
| Cartage @ 1 % of A1 |  |  |  | 4.62
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 735.57
| OVERHEADS & PROFIT @ 15 % |  |  |  | 110.34
| TOTAL |  |  |  | 845.91
| Rate per Set |  |  |  | 845.91
| Say |  |  |  | 846
846
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.23 | 3½ X 150 sq. mm |  |  | DSR Rate Rs. | 1120
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2322 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 150 sq. mm 1.1 KV grade cable | set | 1 | 697.73 | 697.73
| Total cost of materials |  |  |  | 697.73
| Cartage @ 1 % of A1 |  |  |  | 6.9773
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 973.6573
| OVERHEADS & PROFIT @ 15 % |  |  |  | 146.05
| TOTAL |  |  |  | 1119.7073
| Rate per Set |  |  |  | 1119.7073
| Say |  |  |  | 1120
1120
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.24 | 3½ X 185 sq. mm |  |  | DSR Rate Rs. | 1120
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2323 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 185 sq. mm 1.1 KV grade cable | set | 1 | 697.73 | 697.73
| Total cost of materials |  |  |  | 697.73
| Cartage @ 1 % of A1 |  |  |  | 6.9773
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 973.6573
| OVERHEADS & PROFIT @ 15 % |  |  |  | 146.05
| TOTAL |  |  |  | 1119.7073
| Rate per Set |  |  |  | 1119.7073
| Say |  |  |  | 1120
1120
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.25 | 3½ X 225 sq. mm |  |  | DSR Rate Rs. | 1290
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2324 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 225 sq. mm 1.1 KV grade cable | set | 1 | 844.2 | 844.2
| Total cost of materials |  |  |  | 844.2
| Cartage @ 1 % of A1 |  |  |  | 8.442
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1121.592
| OVERHEADS & PROFIT @ 15 % |  |  |  | 168.24
| TOTAL |  |  |  | 1289.832
| Rate per Set |  |  |  | 1289.832
| Say |  |  |  | 1290
1290
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.26 | 3½ X 240 sq. mm |  |  | DSR Rate Rs. | 1290
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2325 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 240 sq. mm 1.1 KV grade cable | set | 1 | 844.2 | 844.2
| Total cost of materials |  |  |  | 844.2
| Cartage @ 1 % of A1 |  |  |  | 8.442
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1121.592
| OVERHEADS & PROFIT @ 15 % |  |  |  | 168.24
| TOTAL |  |  |  | 1289.832
| Rate per Set |  |  |  | 1289.832
| Say |  |  |  | 1290
1290
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.27 | 3½ X 300 sq. mm |  |  | DSR Rate Rs. | 1449
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2326 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 300 sq. mm 1.1 KV grade cable | set | 1 | 844.2 | 844.2
| Total cost of materials |  |  |  | 844.2
| Cartage @ 1 % of A1 |  |  |  | 8.442
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 1260.142
| OVERHEADS & PROFIT @ 15 % |  |  |  | 189.02
| TOTAL |  |  |  | 1449.162
| Rate per Set |  |  |  | 1449.162
| Say |  |  |  | 1449
1449
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.28 | 3½ X 400 sq. mm |  |  | DSR Rate Rs. | 1649
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2327 | Outdoor cable jointing kit with cast resin compound with lugs for 3½ X 400 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 1434.064
| OVERHEADS & PROFIT @ 15 % |  |  |  | 215.11
| TOTAL |  |  |  | 1649.174
| Rate per Set |  |  |  | 1649.174
| Say |  |  |  | 1649
1649
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.29 | 4 X 16 sq. mm |  |  | DSR Rate Rs. | 663
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2328 | Outdoor cable jointing kit with cast resin compound with lugs for 4 X 16 sq. mm 1.1 KV grade cable | set | 1 | 369.08 | 369.08
| Total cost of materials |  |  |  | 369.08
| Cartage @ 1 % of A1 |  |  |  | 3.6908
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 576.5208
| OVERHEADS & PROFIT @ 15 % |  |  |  | 86.48
| TOTAL |  |  |  | 663.0008
| Rate per Set |  |  |  | 663.0008
| Say |  |  |  | 663
663
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.30 | 4 X 25 sq. mm |  |  | DSR Rate Rs. | 663
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2329 | Outdoor cable jointing kit with cast resin compound with lugs for 4 X 25 sq. mm 1.1 KV grade cable | set | 1 | 369.08 | 369.08
| Total cost of materials |  |  |  | 369.08
| Cartage @ 1 % of A1 |  |  |  | 3.6908
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 576.5208
| OVERHEADS & PROFIT @ 15 % |  |  |  | 86.48
| TOTAL |  |  |  | 663.0008
| Rate per Set |  |  |  | 663.0008
| Say |  |  |  | 663
663
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.31 | 4 X 35 sq. mm |  |  | DSR Rate Rs. | 706
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2330 | Outdoor cable jointing kit with cast resin compound with lugs for 4 X 35 sq. mm 1.1 KV grade cable | set | 1 | 405.83 | 405.83
| Total cost of materials |  |  |  | 405.83
| Cartage @ 1 % of A1 |  |  |  | 4.0583
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 613.6383
| OVERHEADS & PROFIT @ 15 % |  |  |  | 92.05
| TOTAL |  |  |  | 705.6883
| Rate per Set |  |  |  | 705.6883
| Say |  |  |  | 706
706
Analysis of rate
9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.2.32 | 4 X 50 sq. mm |  |  | DSR Rate Rs. | 706
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2331 | Outdoor cable jointing kit with cast resin compound with lugs for 4 X 50 sq. mm 1.1 KV grade cable | set | 1 | 405.83 | 405.83
| Total cost of materials |  |  |  | 405.83
| Cartage @ 1 % of A1 |  |  |  | 4.0583
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 613.6383
| OVERHEADS & PROFIT @ 15 % |  |  |  | 92.05
| TOTAL |  |  |  | 705.6883
| Rate per Set |  |  |  | 705.6883
| Say |  |  |  | 706
706
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.1 | 2 X 16 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2332 | Straight through cable jointing kit with cast resin compound with ferrules for 2 X 16 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.2 | 2 X 25 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2333 | Straight through cable jointing kit with cast resin compound with ferrules for 2 X 25 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.3 | 2 X 35 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2334 | Straight through cable jointing kit with cast resin compound with ferrules for 2 X 35 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.4 | 2 X 50 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2335 | Straight through cable jointing kit with cast resin compound with ferrules for 2 X 50 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.5 | 3 X 16 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2336 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 16 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.6 | 3 X 25 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2337 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 25 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.7 | 3 X 35 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2338 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 35 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.8 | 3 X 50 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2339 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 50 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.9 | 3 X 70 sq. mm |  |  | DSR Rate Rs. | 1647
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2340 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 70 sq. mm 1.1 KV grade cable | set | 1 | 1215.9 | 1215.9
| Total cost of materials |  |  |  | 1215.9
| Cartage @ 1 % of A1 |  |  |  | 12.159
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1431.809
| OVERHEADS & PROFIT @ 15 % |  |  |  | 214.77
| TOTAL |  |  |  | 1646.579
| Rate per Set |  |  |  | 1646.579
| Say |  |  |  | 1647
1647
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.10 | 3 X 95 sq. mm |  |  | DSR Rate Rs. | 1760
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2341 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 95 sq. mm 1.1 KV grade cable | set | 1 | 1248.98 | 1248.98
| Total cost of materials |  |  |  | 1248.98
| Cartage @ 1 % of A1 |  |  |  | 12.4898
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1530.4198
| OVERHEADS & PROFIT @ 15 % |  |  |  | 229.56
| TOTAL |  |  |  | 1759.9798
| Rate per Set |  |  |  | 1759.9798
| Say |  |  |  | 1760
1760
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.11 | 3 X 120 sq. mm |  |  | DSR Rate Rs. | 1969
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2342 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 120 sq. mm 1.1 KV grade cable | set | 1 | 1428.53 | 1428.53
| Total cost of materials |  |  |  | 1428.53
| Cartage @ 1 % of A1 |  |  |  | 14.2853
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1711.7653
| OVERHEADS & PROFIT @ 15 % |  |  |  | 256.76
| TOTAL |  |  |  | 1968.5253
| Rate per Set |  |  |  | 1968.5253
| Say |  |  |  | 1969
1969
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.12 | 3 X 150 sq. mm |  |  | DSR Rate Rs. | 1969
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2343 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 150 sq. mm 1.1 KV grade cable | set | 1 | 1428.53 | 1428.53
| Total cost of materials |  |  |  | 1428.53
| Cartage @ 1 % of A1 |  |  |  | 14.2853
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1711.7653
| OVERHEADS & PROFIT @ 15 % |  |  |  | 256.76
| TOTAL |  |  |  | 1968.5253
| Rate per Set |  |  |  | 1968.5253
| Say |  |  |  | 1969
1969
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.13 | 3 X 185 sq. mm |  |  | DSR Rate Rs. | 2331
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2344 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 185 sq. mm 1.1 KV grade cable | set | 1 | 1740.38 | 1740.38
| Total cost of materials |  |  |  | 1740.38
| Cartage @ 1 % of A1 |  |  |  | 17.4038
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2026.7338
| OVERHEADS & PROFIT @ 15 % |  |  |  | 304.01
| TOTAL |  |  |  | 2330.7438
| Rate per Set |  |  |  | 2330.7438
| Say |  |  |  | 2331
2331
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.14 | 3 X 225 sq. mm |  |  | DSR Rate Rs. | 2632
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2345 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 225 sq. mm 1.1 KV grade cable | set | 1 | 1999.73 | 1999.73
| Total cost of materials |  |  |  | 1999.73
| Cartage @ 1 % of A1 |  |  |  | 19.9973
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2288.6773
| OVERHEADS & PROFIT @ 15 % |  |  |  | 343.3
| TOTAL |  |  |  | 2631.9773
| Rate per Set |  |  |  | 2631.9773
| Say |  |  |  | 2632
2632
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.15 | 3 X 240 sq. mm |  |  | DSR Rate Rs. | 2632
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2346 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 240 sq. mm 1.1 KV grade cable | set | 1 | 1999.73 | 1999.73
| Total cost of materials |  |  |  | 1999.73
| Cartage @ 1 % of A1 |  |  |  | 19.9973
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2288.6773
| OVERHEADS & PROFIT @ 15 % |  |  |  | 343.3
| TOTAL |  |  |  | 2631.9773
| Rate per Set |  |  |  | 2631.9773
| Say |  |  |  | 2632
2632
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.16 | 3 X 300 sq. mm |  |  | DSR Rate Rs. | 3393
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2347 | Straight through cable jointing kit with cast resin compound with ferrules for 3 X 300 sq. mm 1.1 KV grade cable | set | 1 | 2517.38 | 2517.38
| Total cost of materials |  |  |  | 2517.38
| Cartage @ 1 % of A1 |  |  |  | 25.1738
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 2950.0538
| OVERHEADS & PROFIT @ 15 % |  |  |  | 442.51
| TOTAL |  |  |  | 3392.5638
| Rate per Set |  |  |  | 3392.5638
| Say |  |  |  | 3393
3393
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.17 | 3½ X 25 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2348 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 25 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.18 | 3½ X 35 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2349 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 35 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.19 | 3½ X 50 sq. mm |  |  | DSR Rate Rs. | 1647
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2350 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 50 sq. mm 1.1 KV grade cable | set | 1 | 1215.9 | 1215.9
| Total cost of materials |  |  |  | 1215.9
| Cartage @ 1 % of A1 |  |  |  | 12.159
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1431.809
| OVERHEADS & PROFIT @ 15 % |  |  |  | 214.77
| TOTAL |  |  |  | 1646.579
| Rate per Set |  |  |  | 1646.579
| Say |  |  |  | 1647
1647
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.20 | 3½ X 70 sq. mm |  |  | DSR Rate Rs. | 1661
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2351 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 70 sq. mm 1.1 KV grade cable | set | 1 | 1227.98 | 1227.98
| Total cost of materials |  |  |  | 1227.98
| Cartage @ 1 % of A1 |  |  |  | 12.2798
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1444.0098
| OVERHEADS & PROFIT @ 15 % |  |  |  | 216.6
| TOTAL |  |  |  | 1660.6098
| Rate per Set |  |  |  | 1660.6098
| Say |  |  |  | 1661
1661
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.21 | 3½ X 95 sq. mm |  |  | DSR Rate Rs. | 1969
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2352 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 95 sq. mm 1.1 KV grade cable | set | 1 | 1428.53 | 1428.53
| Total cost of materials |  |  |  | 1428.53
| Cartage @ 1 % of A1 |  |  |  | 14.2853
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1711.7653
| OVERHEADS & PROFIT @ 15 % |  |  |  | 256.76
| TOTAL |  |  |  | 1968.5253
| Rate per Set |  |  |  | 1968.5253
| Say |  |  |  | 1969
1969
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.22 | 3½ X 120 sq. mm |  |  | DSR Rate Rs. | 2331
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2353 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 120 sq. mm 1.1 KV grade cable | set | 1 | 1740.38 | 1740.38
| Total cost of materials |  |  |  | 1740.38
| Cartage @ 1 % of A1 |  |  |  | 17.4038
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2026.7338
| OVERHEADS & PROFIT @ 15 % |  |  |  | 304.01
| TOTAL |  |  |  | 2330.7438
| Rate per Set |  |  |  | 2330.7438
| Say |  |  |  | 2331
2331
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.23 | 3½ X 150 sq. mm |  |  | DSR Rate Rs. | 2331
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2354 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 150 sq. mm 1.1 KV grade cable | set | 1 | 1740.38 | 1740.38
| Total cost of materials |  |  |  | 1740.38
| Cartage @ 1 % of A1 |  |  |  | 17.4038
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2026.7338
| OVERHEADS & PROFIT @ 15 % |  |  |  | 304.01
| TOTAL |  |  |  | 2330.7438
| Rate per Set |  |  |  | 2330.7438
| Say |  |  |  | 2331
2331
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.24 | 3½ X 185 sq. mm |  |  | DSR Rate Rs. | 2632
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2355 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 185 sq. mm 1.1 KV grade cable | set | 1 | 1999.73 | 1999.73
| Total cost of materials |  |  |  | 1999.73
| Cartage @ 1 % of A1 |  |  |  | 19.9973
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2288.6773
| OVERHEADS & PROFIT @ 15 % |  |  |  | 343.3
| TOTAL |  |  |  | 2631.9773
| Rate per Set |  |  |  | 2631.9773
| Say |  |  |  | 2632
2632
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.25 | 3½ X 225 sq. mm |  |  | DSR Rate Rs. | 2678
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2356 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 225 sq. mm 1.1 KV grade cable | set | 1 | 2039.63 | 2039.63
| Total cost of materials |  |  |  | 2039.63
| Cartage @ 1 % of A1 |  |  |  | 20.3963
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2328.9763
| OVERHEADS & PROFIT @ 15 % |  |  |  | 349.35
| TOTAL |  |  |  | 2678.3263
| Rate per Set |  |  |  | 2678.3263
| Say |  |  |  | 2678
2678
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.26 | 3½ X 240 sq. mm |  |  | DSR Rate Rs. | 3233
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2357 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 240 sq. mm 1.1 KV grade cable | set | 1 | 2517.38 | 2517.38
| Total cost of materials |  |  |  | 2517.38
| Cartage @ 1 % of A1 |  |  |  | 25.1738
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2811.5038
| OVERHEADS & PROFIT @ 15 % |  |  |  | 421.73
| TOTAL |  |  |  | 3233.2338
| Rate per Set |  |  |  | 3233.2338
| Say |  |  |  | 3233
3233
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.27 | 3½ X 300 sq. mm |  |  | DSR Rate Rs. | 3971
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2358 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 300 sq. mm 1.1 KV grade cable | set | 1 | 3015.6 | 3015.6
| Total cost of materials |  |  |  | 3015.6
| Cartage @ 1 % of A1 |  |  |  | 30.156
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 3453.256
| OVERHEADS & PROFIT @ 15 % |  |  |  | 517.99
| TOTAL |  |  |  | 3971.246
| Rate per Set |  |  |  | 3971.246
| Say |  |  |  | 3971
3971
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.28 | 3½ X 400 sq. mm |  |  | DSR Rate Rs. | 2349
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2359 | Straight through cable jointing kit with cast resin compound with ferrules for 3½ X 400 sq. mm 1.1 KV grade cable | set | 1 | 1619.1 | 1619.1
| Total cost of materials |  |  |  | 1619.1
| Cartage @ 1 % of A1 |  |  |  | 16.191
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 2042.791
| OVERHEADS & PROFIT @ 15 % |  |  |  | 306.42
| TOTAL |  |  |  | 2349.211
| Rate per Set |  |  |  | 2349.211
| Say |  |  |  | 2349
2349
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.29 | 4 X 16 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2360 | Straight through cable jointing kit with cast resin compound with ferrules for 4 X 16 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.30 | 4 X 25 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2361 | Straight through cable jointing kit with cast resin compound with ferrules for 4 X 25 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.31 | 4 X 35 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2362 | Straight through cable jointing kit with cast resin compound with ferrules for 4 X 35 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.3 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.3.32 | 4 X 50 sq. mm |  |  | DSR Rate Rs. | 1647
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2363 | Straight through cable jointing kit with cast resin compound with ferrules for 4 X 50 sq. mm 1.1 KV grade cable | set | 1 | 1215.9 | 1215.9
| Total cost of materials |  |  |  | 1215.9
| Cartage @ 1 % of A1 |  |  |  | 12.159
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1431.809
| OVERHEADS & PROFIT @ 15 % |  |  |  | 214.77
| TOTAL |  |  |  | 1646.579
| Rate per Set |  |  |  | 1646.579
| Say |  |  |  | 1647
1647
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.1 | 2 X 16 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2364 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 2 X 16 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.2 | 2 X 25 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2365 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 2 X 25 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.3 | 2 X 35 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2366 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 2 X 35 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.4 | 2 X 50 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2367 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 2 X 50 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.5 | 3 X 16 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2368 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 16 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.6 | 3 X 25 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2369 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 25 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.7 | 3 X 35 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2370 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 35 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.8 | 3 X 50 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2371 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 50 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.9 | 3 X 70 sq. mm |  |  | DSR Rate Rs. | 1685
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2372 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 70 sq. mm 1.1 KV grade cable | set | 1 | 1248.98 | 1248.98
| Total cost of materials |  |  |  | 1248.98
| Cartage @ 1 % of A1 |  |  |  | 12.4898
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1465.2198
| OVERHEADS & PROFIT @ 15 % |  |  |  | 219.78
| TOTAL |  |  |  | 1684.9998
| Rate per Set |  |  |  | 1684.9998
| Say |  |  |  | 1685
1685
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.10 | 3 X 95 sq. mm |  |  | DSR Rate Rs. | 1969
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2373 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 95 sq. mm 1.1 KV grade cable | set | 1 | 1428.53 | 1428.53
| Total cost of materials |  |  |  | 1428.53
| Cartage @ 1 % of A1 |  |  |  | 14.2853
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1711.7653
| OVERHEADS & PROFIT @ 15 % |  |  |  | 256.76
| TOTAL |  |  |  | 1968.5253
| Rate per Set |  |  |  | 1968.5253
| Say |  |  |  | 1969
1969
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.11 | 3 X 120 sq. mm |  |  | DSR Rate Rs. | 1969
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2374 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 120 sq. mm 1.1 KV grade cable | set | 1 | 1428.53 | 1428.53
| Total cost of materials |  |  |  | 1428.53
| Cartage @ 1 % of A1 |  |  |  | 14.2853
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1711.7653
| OVERHEADS & PROFIT @ 15 % |  |  |  | 256.76
| TOTAL |  |  |  | 1968.5253
| Rate per Set |  |  |  | 1968.5253
| Say |  |  |  | 1969
1969
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.12 | 3 X 150 sq. mm |  |  | DSR Rate Rs. | 1969
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2375 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 150 sq. mm 1.1 KV grade cable | set | 1 | 1428.53 | 1428.53
| Total cost of materials |  |  |  | 1428.53
| Cartage @ 1 % of A1 |  |  |  | 14.2853
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1711.7653
| OVERHEADS & PROFIT @ 15 % |  |  |  | 256.76
| TOTAL |  |  |  | 1968.5253
| Rate per Set |  |  |  | 1968.5253
| Say |  |  |  | 1969
1969
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.13 | 3 X 185 sq. mm |  |  | DSR Rate Rs. | 2331
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2376 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 185 sq. mm 1.1 KV grade cable | set | 1 | 1740.38 | 1740.38
| Total cost of materials |  |  |  | 1740.38
| Cartage @ 1 % of A1 |  |  |  | 17.4038
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2026.7338
| OVERHEADS & PROFIT @ 15 % |  |  |  | 304.01
| TOTAL |  |  |  | 2330.7438
| Rate per Set |  |  |  | 2330.7438
| Say |  |  |  | 2331
2331
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.14 | 3 X 225 sq. mm |  |  | DSR Rate Rs. | 2632
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2377 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 225 sq. mm 1.1 KV grade cable | set | 1 | 1999.73 | 1999.73
| Total cost of materials |  |  |  | 1999.73
| Cartage @ 1 % of A1 |  |  |  | 19.9973
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2288.6773
| OVERHEADS & PROFIT @ 15 % |  |  |  | 343.3
| TOTAL |  |  |  | 2631.9773
| Rate per Set |  |  |  | 2631.9773
| Say |  |  |  | 2632
2632
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.15 | 3 X 240 sq. mm |  |  | DSR Rate Rs. | 2678
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2378 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 240 sq. mm 1.1 KV grade cable | set | 1 | 2039.63 | 2039.63
| Total cost of materials |  |  |  | 2039.63
| Cartage @ 1 % of A1 |  |  |  | 20.3963
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2328.9763
| OVERHEADS & PROFIT @ 15 % |  |  |  | 349.35
| TOTAL |  |  |  | 2678.3263
| Rate per Set |  |  |  | 2678.3263
| Say |  |  |  | 2678
2678
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.16 | 3 X 300 sq. mm |  |  | DSR Rate Rs. | 3393
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2379 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3 X 300 sq. mm 1.1 KV grade cable | set | 1 | 2517.38 | 2517.38
| Total cost of materials |  |  |  | 2517.38
| Cartage @ 1 % of A1 |  |  |  | 25.1738
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 2950.0538
| OVERHEADS & PROFIT @ 15 % |  |  |  | 442.51
| TOTAL |  |  |  | 3392.5638
| Rate per Set |  |  |  | 3392.5638
| Say |  |  |  | 3393
3393
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.17 | 3½ X 25 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2380 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 25 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.18 | 3½ X 35 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2381 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 35 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.19 | 3½ X 50 sq. mm |  |  | DSR Rate Rs. | 1647
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2382 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 50 sq. mm 1.1 KV grade cable | set | 1 | 1215.9 | 1215.9
| Total cost of materials |  |  |  | 1215.9
| Cartage @ 1 % of A1 |  |  |  | 12.159
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1431.809
| OVERHEADS & PROFIT @ 15 % |  |  |  | 214.77
| TOTAL |  |  |  | 1646.579
| Rate per Set |  |  |  | 1646.579
| Say |  |  |  | 1647
1647
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.20 | 3½ X 70 sq. mm |  |  | DSR Rate Rs. | 1685
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2383 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 70 sq. mm 1.1 KV grade cable | set | 1 | 1248.98 | 1248.98
| Total cost of materials |  |  |  | 1248.98
| Cartage @ 1 % of A1 |  |  |  | 12.4898
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1465.2198
| OVERHEADS & PROFIT @ 15 % |  |  |  | 219.78
| TOTAL |  |  |  | 1684.9998
| Rate per Set |  |  |  | 1684.9998
| Say |  |  |  | 1685
1685
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.21 | 3½ X 95 sq. mm |  |  | DSR Rate Rs. | 1969
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2384 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 95 sq. mm 1.1 KV grade cable | set | 1 | 1428.53 | 1428.53
| Total cost of materials |  |  |  | 1428.53
| Cartage @ 1 % of A1 |  |  |  | 14.2853
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 1711.7653
| OVERHEADS & PROFIT @ 15 % |  |  |  | 256.76
| TOTAL |  |  |  | 1968.5253
| Rate per Set |  |  |  | 1968.5253
| Say |  |  |  | 1969
1969
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.22 | 3½ X 120 sq. mm |  |  | DSR Rate Rs. | 2331
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2385 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 120 sq. mm 1.1 KV grade cable | set | 1 | 1740.38 | 1740.38
| Total cost of materials |  |  |  | 1740.38
| Cartage @ 1 % of A1 |  |  |  | 17.4038
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2026.7338
| OVERHEADS & PROFIT @ 15 % |  |  |  | 304.01
| TOTAL |  |  |  | 2330.7438
| Rate per Set |  |  |  | 2330.7438
| Say |  |  |  | 2331
2331
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.23 | 3½ X 150 sq. mm |  |  | DSR Rate Rs. | 2331
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2386 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 150 sq. mm 1.1 KV grade cable | set | 1 | 1740.38 | 1740.38
| Total cost of materials |  |  |  | 1740.38
| Cartage @ 1 % of A1 |  |  |  | 17.4038
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2026.7338
| OVERHEADS & PROFIT @ 15 % |  |  |  | 304.01
| TOTAL |  |  |  | 2330.7438
| Rate per Set |  |  |  | 2330.7438
| Say |  |  |  | 2331
2331
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.24 | 3½ X 185 sq. mm |  |  | DSR Rate Rs. | 2632
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2387 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 185 sq. mm 1.1 KV grade cable | set | 1 | 1999.73 | 1999.73
| Total cost of materials |  |  |  | 1999.73
| Cartage @ 1 % of A1 |  |  |  | 19.9973
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2288.6773
| OVERHEADS & PROFIT @ 15 % |  |  |  | 343.3
| TOTAL |  |  |  | 2631.9773
| Rate per Set |  |  |  | 2631.9773
| Say |  |  |  | 2632
2632
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.25 | 3½ X 225 sq. mm |  |  | DSR Rate Rs. | 2632
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2388 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 225 sq. mm 1.1 KV grade cable | set | 1 | 1999.73 | 1999.73
| Total cost of materials |  |  |  | 1999.73
| Cartage @ 1 % of A1 |  |  |  | 19.9973
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2288.6773
| OVERHEADS & PROFIT @ 15 % |  |  |  | 343.3
| TOTAL |  |  |  | 2631.9773
| Rate per Set |  |  |  | 2631.9773
| Say |  |  |  | 2632
2632
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.26 | 3½ X 240 sq. mm |  |  | DSR Rate Rs. | 2678
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2389 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 240 sq. mm 1.1 KV grade cable | set | 1 | 2039.63 | 2039.63
| Total cost of materials |  |  |  | 2039.63
| Cartage @ 1 % of A1 |  |  |  | 20.3963
LABOUR
1002 | Cable jointer | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
| TOTAL |  |  |  | 2328.9763
| OVERHEADS & PROFIT @ 15 % |  |  |  | 349.35
| TOTAL |  |  |  | 2678.3263
| Rate per Set |  |  |  | 2678.3263
| Say |  |  |  | 2678
2678
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.27 | 3½ X 300 sq. mm |  |  | DSR Rate Rs. | 3393
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2390 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 300 sq. mm 1.1 KV grade cable | set | 1 | 2517.38 | 2517.38
| Total cost of materials |  |  |  | 2517.38
| Cartage @ 1 % of A1 |  |  |  | 25.1738
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 2950.0538
| OVERHEADS & PROFIT @ 15 % |  |  |  | 442.51
| TOTAL |  |  |  | 3392.5638
| Rate per Set |  |  |  | 3392.5638
| Say |  |  |  | 3393
3393
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.28 | 3½ X 400 sq. mm |  |  | DSR Rate Rs. | 4788
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2391 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 3½ X 400 sq. mm 1.1 KV grade cable | set | 1 | 3719.1 | 3719.1
| Total cost of materials |  |  |  | 3719.1
| Cartage @ 1 % of A1 |  |  |  | 37.191
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 4163.791
| OVERHEADS & PROFIT @ 15 % |  |  |  | 624.57
| TOTAL |  |  |  | 4788.361
| Rate per Set |  |  |  | 4788.361
| Say |  |  |  | 4788
4788
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.29 | 4 X 16 sq. mm |  |  | DSR Rate Rs. | 1245
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2392 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 4 X 16 sq. mm 1.1 KV grade cable | set | 1 | 870.45 | 870.45
| Total cost of materials |  |  |  | 870.45
| Cartage @ 1 % of A1 |  |  |  | 8.7045
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1082.9045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 162.44
| TOTAL |  |  |  | 1245.3445
| Rate per Set |  |  |  | 1245.3445
| Say |  |  |  | 1245
1245
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.30 | 4 X 25 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2393 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 4 X 25 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.31 | 4 X 35 sq. mm |  |  | DSR Rate Rs. | 1415
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2394 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 4 X 35 sq. mm 1.1 KV grade cable | set | 1 | 1016.4 | 1016.4
| Total cost of materials |  |  |  | 1016.4
| Cartage @ 1 % of A1 |  |  |  | 10.164
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1230.314
| OVERHEADS & PROFIT @ 15 % |  |  |  | 184.55
| TOTAL |  |  |  | 1414.864
| Rate per Set |  |  |  | 1414.864
| Say |  |  |  | 1415
1415
Analysis of rate
9.4 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.4.32 | 4 X 50 sq. mm |  |  | DSR Rate Rs. | 1647
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2395 | Straight through cable jointing kit with heat shrinkable kit with ferrules for 4 X 50 sq. mm 1.1 KV grade cable | set | 1 | 1215.9 | 1215.9
| Total cost of materials |  |  |  | 1215.9
| Cartage @ 1 % of A1 |  |  |  | 12.159
LABOUR
1002 | Cable jointer | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1431.809
| OVERHEADS & PROFIT @ 15 % |  |  |  | 214.77
| TOTAL |  |  |  | 1646.579
| Rate per Set |  |  |  | 1646.579
| Say |  |  |  | 1647
1647
CHAPTER 10 – HV CABLE JOINTING & END TERMINATION (Analysis of rate based on DAR)
Analysis of rate
10.1 | Supplying and making indoor cable end jointing with cast resin compound, including lugs and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.1.1 | 70 sq. mm |  |  | DSR Rate Rs. | 1078
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2413 | Indoor cable jointing kit with cast resin compound with lugs for 11 KV grade XLPE cable for 3 core 70 sq. mm. | set | 1 | 524.48 | 524.48
| Total cost of materials |  |  |  | 524.48
| Cartage @ 1 % of A1 |  |  |  | 5.2448
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 937.2248
| OVERHEADS & PROFIT @ 15 % |  |  |  | 140.58
| TOTAL |  |  |  | 1077.8048
| Rate per Set |  |  |  | 1077.8048
| Say |  |  |  | 1078
1078
Analysis of rate
10.1 | Supplying and making indoor cable end jointing with cast resin compound, including lugs and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.1.2 | 120 sq. mm |  |  | DSR Rate Rs. | 1359
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2414 | Indoor cable jointing kit with cast resin compound with lugs for 11 KV grade XLPE cable for 3 core 120 sq. mm. | set | 1 | 524.48 | 524.48
| Total cost of materials |  |  |  | 524.48
| Cartage @ 1 % of A1 |  |  |  | 5.2448
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 1181.7248
| OVERHEADS & PROFIT @ 15 % |  |  |  | 177.26
| TOTAL |  |  |  | 1358.9848
| Rate per Set |  |  |  | 1358.9848
| Say |  |  |  | 1359
1359
Analysis of rate
10.1 | Supplying and making indoor cable end jointing with cast resin compound, including lugs and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.1.3 | 240 sq. mm |  |  | DSR Rate Rs. | 1826
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2415 | Indoor cable jointing kit with cast resin compound with lugs for 11 KV grade XLPE cable for 3 core 240 sq. mm. | set | 1 | 765.45 | 765.45
| Total cost of materials |  |  |  | 765.45
| Cartage @ 1 % of A1 |  |  |  | 7.6545
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 1588.1045
| OVERHEADS & PROFIT @ 15 % |  |  |  | 238.22
| TOTAL |  |  |  | 1826.3245
| Rate per Set |  |  |  | 1826.3245
| Say |  |  |  | 1826
1826
Analysis of rate
10.1 | Supplying and making indoor cable end jointing with cast resin compound, including lugs and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.1.4 | 300 sq. mm |  |  | DSR Rate Rs. | 1859
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2416 | Indoor cable jointing kit with cast resin compound with lugs for 11 KV grade XLPE cable for 3 core 300 sq. mm. | set | 1 | 793.8 | 793.8
| Total cost of materials |  |  |  | 793.8
| Cartage @ 1 % of A1 |  |  |  | 7.938
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 1616.738
| OVERHEADS & PROFIT @ 15 % |  |  |  | 242.51
| TOTAL |  |  |  | 1859.248
| Rate per Set |  |  |  | 1859.248
| Say |  |  |  | 1859
1859
Analysis of rate
10.2 | Supplying and making outdoor cable end jointing with cast resin compound, including lugs and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.2.1 | 70 sq. mm |  |  | DSR Rate Rs. | 2554
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2417 | Outdoor cable jointing kit with cast resin compound with lugs for 11 KV grade XLPE cable for 3 core 70 sq. mm. | set | 1 | 1795.5 | 1795.5
| Total cost of materials |  |  |  | 1795.5
| Cartage @ 1 % of A1 |  |  |  | 17.955
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 2220.955
| OVERHEADS & PROFIT @ 15 % |  |  |  | 333.14
| TOTAL |  |  |  | 2554.095
| Rate per Set |  |  |  | 2554.095
| Say |  |  |  | 2554
2554
Analysis of rate
10.2 | Supplying and making outdoor cable end jointing with cast resin compound, including lugs and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.2.2 | 120 sq. mm |  |  | DSR Rate Rs. | 2863
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2418 | Outdoor cable jointing kit with cast resin compound with lugs for 11 KV grade XLPE cable for 3 core 120 sq. mm. | set | 1 | 1819.13 | 1819.13
| Total cost of materials |  |  |  | 1819.13
| Cartage @ 1 % of A1 |  |  |  | 18.1913
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 2489.3213
| OVERHEADS & PROFIT @ 15 % |  |  |  | 373.4
| TOTAL |  |  |  | 2862.7213
| Rate per Set |  |  |  | 2862.7213
| Say |  |  |  | 2863
2863
Analysis of rate
10.2 | Supplying and making outdoor cable end jointing with cast resin compound, including lugs and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.2.3 | 240 sq. mm |  |  | DSR Rate Rs. | 3330
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2419 | Outdoor cable jointing kit with cast resin compound with lugs for 11 KV grade XLPE cable for 3 core 240 sq. mm. | set | 1 | 2060.1 | 2060.1
| Total cost of materials |  |  |  | 2060.1
| Cartage @ 1 % of A1 |  |  |  | 20.601
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 2895.701
| OVERHEADS & PROFIT @ 15 % |  |  |  | 434.36
| TOTAL |  |  |  | 3330.061
| Rate per Set |  |  |  | 3330.061
| Say |  |  |  | 3330
3330
Analysis of rate
10.2 | Supplying and making outdoor cable end jointing with cast resin compound, including lugs and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.2.4 | 300 sq. mm |  |  | DSR Rate Rs. | 3330
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2420 | Outdoor cable jointing kit with cast resin compound with lugs for 11 KV grade XLPE cable for 3 core 300 sq. mm. | set | 1 | 2060.1 | 2060.1
| Total cost of materials |  |  |  | 2060.1
| Cartage @ 1 % of A1 |  |  |  | 20.601
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 2895.701
| OVERHEADS & PROFIT @ 15 % |  |  |  | 434.36
| TOTAL |  |  |  | 3330.061
| Rate per Set |  |  |  | 3330.061
| Say |  |  |  | 3330
3330
Analysis of rate
10.3 | Supplying and making straight through cable jointing with cast resin compound, including ferrule and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.3.1 | 70 sq. mm |  |  | DSR Rate Rs. | 2385
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2421 | Straight through cable jointing kit with cast resin compound with ferrules for 11 KV grade XLPE cable for 3 core 70 sq. mm. | set | 1 | 1408.05 | 1408.05
| Total cost of materials |  |  |  | 1408.05
| Cartage @ 1 % of A1 |  |  |  | 14.0805
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 2074.1305
| OVERHEADS & PROFIT @ 15 % |  |  |  | 311.12
| TOTAL |  |  |  | 2385.2505
| Rate per Set |  |  |  | 2385.2505
| Say |  |  |  | 2385
2385
Analysis of rate
10.3 | Supplying and making straight through cable jointing with cast resin compound, including ferrule and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.3.2 | 120 sq. mm |  |  | DSR Rate Rs. | 2720
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2422 | Straight through cable jointing kit with cast resin compound with ferrules for 11 KV grade XLPE cable for 3 core 120 sq. mm. | set | 1 | 1696.28 | 1696.28
| Total cost of materials |  |  |  | 1696.28
| Cartage @ 1 % of A1 |  |  |  | 16.9628
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 2365.2428
| OVERHEADS & PROFIT @ 15 % |  |  |  | 354.79
| TOTAL |  |  |  | 2720.0328
| Rate per Set |  |  |  | 2720.0328
| Say |  |  |  | 2720
2720
Analysis of rate
10.3 | Supplying and making straight through cable jointing with cast resin compound, including ferrule and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.3.3 | 240 sq. mm |  |  | DSR Rate Rs. | 4054
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2423 | Straight through cable jointing kit with cast resin compound with ferrules for 11 KV grade XLPE cable for 3 core 240 sq. mm. | set | 1 | 2683.8 | 2683.8
| Total cost of materials |  |  |  | 2683.8
| Cartage @ 1 % of A1 |  |  |  | 26.838
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 3525.638
| OVERHEADS & PROFIT @ 15 % |  |  |  | 528.85
| TOTAL |  |  |  | 4054.488
| Rate per Set |  |  |  | 4054.488
| Say |  |  |  | 4054
4054
Analysis of rate
10.3 | Supplying and making straight through cable jointing with cast resin compound, including ferrule and other jointing materials, for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.3.4 | 300 sq. mm |  |  | DSR Rate Rs. | 4631
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2424 | Straight through cable jointing kit with cast resin compound with ferrules for 11 KV grade XLPE cable for 3 core 300 sq. mm. | set | 1 | 3179.93 | 3179.93
| Total cost of materials |  |  |  | 3179.93
| Cartage @ 1 % of A1 |  |  |  | 31.7993
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 4026.7293
| OVERHEADS & PROFIT @ 15 % |  |  |  | 604.01
| TOTAL |  |  |  | 4630.7393
| Rate per Set |  |  |  | 4630.7393
| Say |  |  |  | 4631
4631
Analysis of rate
10.4 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.4.1 | 70 sq. mm |  |  | DSR Rate Rs. | 4667
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2437 | Indoor heat shrinkable cable jointing kit with lugs for 11 KV grade XLPE cable for 3 core 70 sq. mm. | set | 1 | 3614.63 | 3614.63
| Total cost of materials |  |  |  | 3614.63
| Cartage @ 1 % of A1 |  |  |  | 36.1463
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 4058.2763
| OVERHEADS & PROFIT @ 15 % |  |  |  | 608.74
| TOTAL |  |  |  | 4667.0163
| Rate per Set |  |  |  | 4667.0163
| Say |  |  |  | 4667
4667
Analysis of rate
10.4 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.4.2 | 120 sq. mm |  |  | DSR Rate Rs. | 4948
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2438 | Indoor heat shrinkable cable jointing kit with lugs for 11 KV grade XLPE cable for 3 core 120 sq. mm. | set | 1 | 3614.63 | 3614.63
| Total cost of materials |  |  |  | 3614.63
| Cartage @ 1 % of A1 |  |  |  | 36.1463
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 4302.7763
| OVERHEADS & PROFIT @ 15 % |  |  |  | 645.42
| TOTAL |  |  |  | 4948.1963
| Rate per Set |  |  |  | 4948.1963
| Say |  |  |  | 4948
4948
Analysis of rate
10.4 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.4.3 | 240 sq. mm |  |  | DSR Rate Rs. | 6457
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2439 | Indoor heat shrinkable cable jointing kit with lugs for 11 KV grade XLPE cable for 3 core 240 sq. mm. | set | 1 | 4752.56 | 4752.56
| Total cost of materials |  |  |  | 4752.56
| Cartage @ 1 % of A1 |  |  |  | 47.5256
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 5615.0856
| OVERHEADS & PROFIT @ 15 % |  |  |  | 842.26
| TOTAL |  |  |  | 6457.3456
| Rate per Set |  |  |  | 6457.3456
| Say |  |  |  | 6457
6457
Analysis of rate
10.4 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.4.4 | 300 sq. mm |  |  | DSR Rate Rs. | 6457
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2440 | Indoor heat shrinkable cable jointing kit with lugs for 11 KV grade XLPE cable for 3 core 300 sq. mm. | set | 1 | 4752.56 | 4752.56
| Total cost of materials |  |  |  | 4752.56
| Cartage @ 1 % of A1 |  |  |  | 47.5256
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 5615.0856
| OVERHEADS & PROFIT @ 15 % |  |  |  | 842.26
| TOTAL |  |  |  | 6457.3456
| Rate per Set |  |  |  | 6457.3456
| Say |  |  |  | 6457
6457
Analysis of rate
10.5 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.5.1 | 70 sq. mm |  |  | DSR Rate Rs. | 7984
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2441 | Outdoor heat shrinkable cable jointing kit with lugs for 11 KV grade XLPE cable for 3 core 70 sq. mm. | set | 1 | 6470.63 | 6470.63
| Total cost of materials |  |  |  | 6470.63
| Cartage @ 1 % of A1 |  |  |  | 64.7063
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 6942.8363
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1041.43
| TOTAL |  |  |  | 7984.2663
| Rate per Set |  |  |  | 7984.2663
| Say |  |  |  | 7984
7984
Analysis of rate
10.5 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.5.2 | 120 sq. mm |  |  | DSR Rate Rs. | 8265
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2442 | Outdoor heat shrinkable cable jointing kit with lugs for 11 KV grade XLPE cable for 3 core 120 sq. mm. | set | 1 | 6470.63 | 6470.63
| Total cost of materials |  |  |  | 6470.63
| Cartage @ 1 % of A1 |  |  |  | 64.7063
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 7187.3363
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1078.1
| TOTAL |  |  |  | 8265.4363
| Rate per Set |  |  |  | 8265.4363
| Say |  |  |  | 8265
8265
Analysis of rate
10.5 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.5.3 | 240 sq. mm |  |  | DSR Rate Rs. | 9464
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2443 | Outdoor heat shrinkable cable jointing kit with lugs for 11 KV grade XLPE cable for 3 core 240 sq. mm. | set | 1 | 7340.81 | 7340.81
| Total cost of materials |  |  |  | 7340.81
| Cartage @ 1 % of A1 |  |  |  | 73.4081
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 8229.2181
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1234.38
| TOTAL |  |  |  | 9463.5981
| Rate per Set |  |  |  | 9463.5981
| Say |  |  |  | 9464
9464
Analysis of rate
10.5 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.5.4 | 300 sq. mm |  |  | DSR Rate Rs. | 9464
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2444 | Outdoor heat shrinkable cable jointing kit with lugs for 11 KV grade XLPE cable for 3 core 300 sq. mm. | set | 1 | 7340.81 | 7340.81
| Total cost of materials |  |  |  | 7340.81
| Cartage @ 1 % of A1 |  |  |  | 73.4081
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 8229.2181
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1234.38
| TOTAL |  |  |  | 9463.5981
| Rate per Set |  |  |  | 9463.5981
| Say |  |  |  | 9464
9464
Analysis of rate
10.6 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.6.1 | 70 sq. mm |  |  | DSR Rate Rs. | 9250
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2445 | Straight through heat shrinkable cable jointing kit with ferrules for 11 KV grade XLPE cable for 3 core 70 sq. mm. | set | 1 | 7318.5 | 7318.5
| Total cost of materials |  |  |  | 7318.5
| Cartage @ 1 % of A1 |  |  |  | 73.185
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 8043.685
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1206.55
| TOTAL |  |  |  | 9250.235
| Rate per Set |  |  |  | 9250.235
| Say |  |  |  | 9250
9250
Analysis of rate
10.6 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.6.2 | 120 sq. mm |  |  | DSR Rate Rs. | 9955
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2446 | Straight through heat shrinkable cable jointing kit with ferrules for 11 KV grade XLPE cable for 3 core 120 sq. mm. | set | 1 | 7925.4 | 7925.4
| Total cost of materials |  |  |  | 7925.4
| Cartage @ 1 % of A1 |  |  |  | 79.254
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 8656.654
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1298.5
| TOTAL |  |  |  | 9955.154
| Rate per Set |  |  |  | 9955.154
| Say |  |  |  | 9955
9955
Analysis of rate
10.6 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.6.3 | 240 sq. mm |  |  | DSR Rate Rs. | 10640
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2447 | Straight through heat shrinkable cable jointing kit with ferrules for 11 KV grade XLPE cable for 3 core 240 sq. mm. | set | 1 | 8353.8 | 8353.8
| Total cost of materials |  |  |  | 8353.8
| Cartage @ 1 % of A1 |  |  |  | 83.538
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 9252.338
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1387.85
| TOTAL |  |  |  | 10640.188
| Rate per Set |  |  |  | 10640.188
| Say |  |  |  | 10640
10640
Analysis of rate
10.6 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
10.6.4 | 300 sq. mm |  |  | DSR Rate Rs. | 10640
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2448 | Straight through heat shrinkable cable jointing kit with ferrules for 11 KV grade XLPE cable for 3 core 300 sq. mm. | set | 1 | 8353.8 | 8353.8
| Total cost of materials |  |  |  | 8353.8
| Cartage @ 1 % of A1 |  |  |  | 83.538
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 9252.338
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1387.85
| TOTAL |  |  |  | 10640.188
| Rate per Set |  |  |  | 10640.188
| Say |  |  |  | 10640
10640
Analysis of rate
10.7 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required :
10.7.1 | 70 sq. mm |  |  | DSR Rate Rs. | 10369
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2528 | Indoor heat shrinkable cable jointing kit with lugs for 33 KV grade XLPE cable for 3 core 70 sq. mm. | set | 1 | 8523.38 | 8523.38
| Total cost of materials |  |  |  | 8523.38
| Cartage @ 1 % of A1 |  |  |  | 85.2338
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 9016.1138
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1352.42
| TOTAL |  |  |  | 10368.5338
| Rate per Set |  |  |  | 10368.5338
| Say |  |  |  | 10369
10369
Analysis of rate
10.7 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required :
10.7.2 | 120 sq. mm |  |  | DSR Rate Rs. | 14283
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2529 | Indoor heat shrinkable cable jointing kit with lugs for 33 KV grade XLPE cable for 3 core 120 sq. mm. | set | 1 | 11651.59 | 11651.59
| Total cost of materials |  |  |  | 11651.59
| Cartage @ 1 % of A1 |  |  |  | 116.5159
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 12420.1059
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1863.02
| TOTAL |  |  |  | 14283.1259
| Rate per Set |  |  |  | 14283.1259
| Say |  |  |  | 14283
14283
Analysis of rate
10.7 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required :
10.7.3 | 240 sq. mm |  |  | DSR Rate Rs. | 15518
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2530 | Indoor heat shrinkable cable jointing kit with lugs for 33 KV grade XLPE cable for 3 core 240 sq. mm. | set | 1 | 12553.01 | 12553.01
| Total cost of materials |  |  |  | 12553.01
| Cartage @ 1 % of A1 |  |  |  | 125.5301
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 13493.5401
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2024.03
| TOTAL |  |  |  | 15517.5701
| Rate per Set |  |  |  | 15517.5701
| Say |  |  |  | 15518
15518
Analysis of rate
10.8 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required :
10.8.1 | 70 sq. mm |  |  | DSR Rate Rs. | 15479
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2531 | Outdoor heat shrinkable cable jointing kit with lugs for 33 KV grade XLPE cable for 3 core 70 sq. mm. | set | 1 | 12923.4 | 12923.4
| Total cost of materials |  |  |  | 12923.4
| Cartage @ 1 % of A1 |  |  |  | 129.234
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 13460.134
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2019.02
| TOTAL |  |  |  | 15479.154
| Rate per Set |  |  |  | 15479.154
| Say |  |  |  | 15479
15479
Analysis of rate
10.8 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required :
10.8.2 | 120 sq. mm |  |  | DSR Rate Rs. | 18777
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2532 | Outdoor heat shrinkable cable jointing kit with lugs for 33 KV grade XLPE cable for 3 core 120 sq. mm. | set | 1 | 15520.58 | 15520.58
| Total cost of materials |  |  |  | 15520.58
| Cartage @ 1 % of A1 |  |  |  | 155.2058
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 16327.7858
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2449.17
| TOTAL |  |  |  | 18776.9558
| Rate per Set |  |  |  | 18776.9558
| Say |  |  |  | 18777
18777
Analysis of rate
10.8 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required :
10.8.3 | 240 sq. mm |  |  | DSR Rate Rs. | 21224
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2533 | Outdoor heat shrinkable cable jointing kit with lugs for 33 KV grade XLPE cable for 3 core 240 sq. mm. | set | 1 | 17466.23 | 17466.23
| Total cost of materials |  |  |  | 17466.23
| Cartage @ 1 % of A1 |  |  |  | 174.6623
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 18455.8923
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2768.38
| TOTAL |  |  |  | 21224.2723
| Rate per Set |  |  |  | 21224.2723
| Say |  |  |  | 21224
21224
Analysis of rate
10.9 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required :
10.9.1 | 70 sq. mm |  |  | DSR Rate Rs. | 24311
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2534 | Straight through heat shrinkable cable jointing kit with ferrules for 33 KV grade XLPE cable for 3 core 70 sq. mm. | set | 1 | 20527.5 | 20527.5
| Total cost of materials |  |  |  | 20527.5
| Cartage @ 1 % of A1 |  |  |  | 205.275
LABOUR
1002 | Cable jointer | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 21140.275
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3171.04
| TOTAL |  |  |  | 24311.315
| Rate per Set |  |  |  | 24311.315
| Say |  |  |  | 24311
24311
Analysis of rate
10.9 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required :
10.9.2 | 120 sq. mm |  |  | DSR Rate Rs. | 30911
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2535 | Straight through heat shrinkable cable jointing kit with ferrules for 33 KV grade XLPE cable for 3 core 120 sq. mm. | set | 1 | 25967.29 | 25967.29
| Total cost of materials |  |  |  | 25967.29
| Cartage @ 1 % of A1 |  |  |  | 259.6729
LABOUR
1002 | Cable jointer | day | 0.8 | 447 | 357.6
1007 | Khallasi | day | 0.8 | 368 | 294.4
| TOTAL |  |  |  | 26878.9629
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4031.84
| TOTAL |  |  |  | 30910.8029
| Rate per Set |  |  |  | 30910.8029
| Say |  |  |  | 30911
30911
Analysis of rate
10.9 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required :
10.9.3 | 240 sq. mm |  |  | DSR Rate Rs. | 43180
Details of cost for 1 Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2536 | Straight through heat shrinkable cable jointing kit with ferrules for 33 KV grade XLPE cable for 3 core 240 sq. mm. | set | 1 | 36369.38 | 36369.38
| Total cost of materials |  |  |  | 36369.38
| Cartage @ 1 % of A1 |  |  |  | 363.6938
LABOUR
1002 | Cable jointer | day | 1 | 447 | 447
1007 | Khallasi | day | 1 | 368 | 368
| TOTAL |  |  |  | 37548.0738
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5632.21
| TOTAL |  |  |  | 43180.2838
| Rate per Set |  |  |  | 43180.2838
| Say |  |  |  | 43180
43180
CHAPTER 11 – POLE ERECTION (Analysis of rate based on DAR)
Analysis of rate
11.1 | Erection of RCC/ PCC pole of following length in brick ballast and ramming the foundation, finishing with 150mm thick cement concrete (1:3:6) layer on top with including excavation and refilling etc as required.
11.1.1 | Above 4.5 metre and upto 6.5 metre |  |  | DSR Rate Rs. | 2878
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2947 | Bricks ballast | cum | 0.46 | 525 | 241.5
= 0.44+ 0.02 (wastage@5%) = 0.46 cum
| Total cost of materials |  |  |  | 241.5
| Cartage @ 1 % of A1 |  |  |  | 2.415
LABOUR
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 3.66 | 368 | 1346.88
1013 | Bhisti | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 1931.495
| OVERHEADS & PROFIT @ 15 % |  |  |  | 289.72
| TOTAL |  |  |  | 2221.215
14.4 | Excavation including refilling as required | cum | 1.07 | 318 | 340.26
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.07 | 4525 | 316.75
| TOTAL |  |  |  | 2878.225
| Rate per Each |  |  |  | 2878.225
| Say |  |  |  | 2878
2878
Analysis of rate
11.1 | Erection of RCC/ PCC pole of following length in brick ballast and ramming the foundation, finishing with 150mm thick cement concrete (1:3:6) layer on top with including excavation and refilling etc as required.
11.1.2 | Above 6.5 metre and upto 8.0 metre |  |  | DSR Rate Rs. | 3200
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2947 | Bricks ballast | cum | 0.6 | 525 | 315
= 0.57+ 0.03(wastage @5%) = 0.60 cum
| Total cost of materials |  |  |  | 315
| Cartage @ 1 % of A1 |  |  |  | 3.15
LABOUR
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 4 | 368 | 1472
1013 | Bhisti | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2130.85
| OVERHEADS & PROFIT @ 15 % |  |  |  | 319.63
| TOTAL |  |  |  | 2450.48
14.4 | Excavation including refilling as required | cum | 1.36 | 318 | 432.48
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.07 | 4525 | 316.75
| TOTAL |  |  |  | 3199.71
| Rate per Each |  |  |  | 3199.71
| Say |  |  |  | 3200
3200
Analysis of rate
11.1 | Erection of RCC/ PCC pole of following length in brick ballast and ramming the foundation, finishing with 150mm thick cement concrete (1:3:6) layer on top with including excavation and refilling etc as required.
11.1.3 | Above 8.0 metre and upto 11.0 metre |  |  | DSR Rate Rs. | 3826
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2947 | Bricks ballast | cum | 0.74 | 525 | 388.5
= 0.70+ 0.04 (wastage @5%) = 0.74 cum
| Total cost of materials |  |  |  | 388.5
| Cartage @ 1 % of A1 |  |  |  | 3.885
LABOUR
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 5 | 368 | 1840
1013 | Bhisti | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2573.085
| OVERHEADS & PROFIT @ 15 % |  |  |  | 385.96
| TOTAL |  |  |  | 2959.045
14.4 | Excavation including refilling as required | cum | 1.73 | 318 | 550.14
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.07 | 4525 | 316.75
| TOTAL |  |  |  | 3825.935
| Rate per Each |  |  |  | 3825.935
| Say |  |  |  | 3826
3826
Analysis of rate
11.1 | Erection of RCC/ PCC pole of following length in brick ballast and ramming the foundation, finishing with 150mm thick cement concrete (1:3:6) layer on top with including excavation and refilling etc as required.
11.1.4 | Above 11.00 metre and upto 13.00 metre |  |  | DSR Rate Rs. | 4209
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2947 | Bricks ballast | cum | 0.92 | 525 | 483
= 0.88+ 0.04 (wastage @5%) = 0.92 cum Total cost of materials
| Total cost of materials |  |  |  | 483
| Cartage @ 1 % of A1 |  |  |  | 4.83
LABOUR
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 5.33 | 368 | 1961.44
1013 | Bhisti | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 2789.97
| OVERHEADS & PROFIT @ 15 % |  |  |  | 418.5
| TOTAL |  |  |  | 3208.47
14.4 | Excavation including refilling as required | cum | 2.15 | 318 | 683.7
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.07 | 4525 | 316.75
| TOTAL |  |  |  | 4208.92
| Rate per Each |  |  |  | 4208.92
| Say |  |  |  | 4209
4209
Analysis of rate
11.2 | Erection of RCC/ PCC pole strut in brick ballast and ramming the foundation including excavation and refilling and secured with holding clamps, bolts, nuts, etc. as required.
|  |  |  | DSR Rate Rs. | 4891
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2947 | Bricks ballast | cum | 0.56 | 525 | 294
= 0.53+ 0.03 (wastage @5%) = 0.56 cum
2924 | Clamps, bolts, nuts etc. | set | 1 | 93 | 93
| Total cost of materials |  |  |  | 387
| Cartage @ 1 % of A1 |  |  |  | 3.87
LABOUR
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1003 | Lineman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 7.5 | 368 | 2760
1013 | Bhisti | day | 0.16 | 368 | 58.88
| TOTAL |  |  |  | 3567.56
| OVERHEADS & PROFIT @ 15 % |  |  |  | 535.13
| TOTAL |  |  |  | 4102.69
14.4 | Excavation including refilling as required | cum | 1.34 | 318 | 426.12
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.08 | 4525 | 362
| TOTAL |  |  |  | 4890.81
| Rate per Each |  |  |  | 4890.81
| Say |  |  |  | 4891
4891
Analysis of rate
11.3 | Erection of metallic pole of following length in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling etc. as required.
11.3.1 | Above 4.5 metre and upto 6.5 metre |  |  | DSR Rate Rs. | 2760
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 3 | 368 | 1104
| TOTAL |  |  |  | 1385.82
| OVERHEADS & PROFIT @ 15 % |  |  |  | 207.87
| TOTAL |  |  |  | 1593.69
14.4 | Excavation including refilling as required | cum | 0.68 | 318 | 216.24
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.21 | 4525 | 950.25
| TOTAL |  |  |  | 2760.18
| Rate per Each |  |  |  | 2760.18
| Say |  |  |  | 2760
2760
Analysis of rate
11.3 | Erection of metallic pole of following length in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling etc. as required.
11.3.2 | Above 6.5 metre and upto 8.0 metre |  |  | DSR Rate Rs. | 3322
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 3.33 | 368 | 1225.44
| TOTAL |  |  |  | 1507.26
| OVERHEADS & PROFIT @ 15 % |  |  |  | 226.09
| TOTAL |  |  |  | 1733.35
14.4 | Excavation including refilling as required | cum | 0.87 | 318 | 276.66
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.29 | 4525 | 1312.25
| TOTAL |  |  |  | 3322.26
| Rate per Each |  |  |  | 3322.26
| Say |  |  |  | 3322
3322
Analysis of rate
11.3 | Erection of metallic pole of following length in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling etc. as required.
11.3.3 | Above 8.0 metre and upto 11.0 metre |  |  | DSR Rate Rs. | 3930
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 3.66 | 368 | 1346.88
| TOTAL |  |  |  | 1628.7
| OVERHEADS & PROFIT @ 15 % |  |  |  | 244.31
| TOTAL |  |  |  | 1873.01
14.4 | Excavation including refilling as required | cum | 1.06 | 318 | 337.08
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.38 | 4525 | 1719.5
| TOTAL |  |  |  | 3929.59
| Rate per Each |  |  |  | 3929.59
| Say |  |  |  | 3930
3930
Analysis of rate
11.3 | Erection of metallic pole of following length in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling etc. as required.
11.3.4 | Above 11.00 metre and upto 13.00 metre |  |  | DSR Rate Rs. | 4593
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 1753.82
| OVERHEADS & PROFIT @ 15 % |  |  |  | 263.07
| TOTAL |  |  |  | 2016.89
14.4 | Excavation including refilling as required | cum | 1.27 | 318 | 403.86
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.48 | 4525 | 2172
| TOTAL |  |  |  | 4592.75
| Rate per Each |  |  |  | 4592.75
| Say |  |  |  | 4593
4593
Analysis of rate
11.4 | Erection of steel tubular or rail pole strut in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling and secured with holding clamps, bolts, nuts, etc. as required.
|  |  |  | DSR Rate Rs. | 4688
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2924 | Clamps, bolts, nuts etc. | set | 1 | 93 | 93
| Total cost of materials |  |  |  | 93
| Cartage @ 1 % of A1 |  |  |  | 0.93
LABOUR
1010 | Mason, Grade 2 | day | 0.33 | 407 | 134.31
1003 | Lineman | day | 0.5 | 447 | 223.5
1007 | Khallasi | day | 5.5 | 368 | 2024
| TOTAL |  |  |  | 2475.74
| OVERHEADS & PROFIT @ 15 % |  |  |  | 371.36
| TOTAL |  |  |  | 2847.1
14.4 | Excavation including refilling as required | cum | 0.95 | 318 | 302.1
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.34 | 4525 | 1538.5
| TOTAL |  |  |  | 4687.7
| Rate per Each |  |  |  | 4687.7
| Say |  |  |  | 4688
4688
Analysis of rate
11.5 | Providing and making steel pole collar with cement concrete (1 cement : 3 coarse sand : 6 stone aggregate 20mm) of specified size and shape including form work, plastering if required, curing etc as required. (volume of pole/ pipe not to be deducted)
|  |  |  | DSR Rate Rs. | 4693
Details of cost for 1 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2950 | Stone aggregate (single size) 20mm nominal size | cum | 0.7 | 1175 | 822.5
2951 | Stone aggregate (single size) 10mm nominal size | cum | 0.24 | 1175 | 282
2952 | Coarse sand (Zone III) | cum | 0.47 | 1200 | 564
2948 | Cement | tonne | 0.22 | 5250 | 1155
| Total cost of materials |  |  |  | 2823.5
| Cartage @ 1 % of A1 |  |  |  | 28.235
LABOUR
1010 | Mason, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 1.8 | 368 | 662.4
1013 | Bhisti | day | 1 | 368 | 368
9999 | Sundries | L.S. | 70 | 1.1 | 77
| TOTAL |  |  |  | 4040.535
| Add 1% for water charges |  |  |  | 40.123
| TOTAL |  |  |  | 4080.658
| OVERHEADS & PROFIT @ 15 % |  |  |  | 612.1
| TOTAL |  |  |  | 4692.758
| Rate per cum |  |  |  | 4692.758
| Say |  |  |  | 4693
4693
Analysis of rate
11.6 | Supplying and embedding following dia G.I. pipe (medium class) in pole collar/ foundation (during casting) for cable entry including bending the pipe to the required shape complete as required.
11.6.1 | 32 mm dia |  |  | DSR Rate Rs. | 243
Details of cost for 2 metre long 1 No pipe
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2831 | 32 mm dia. G.I. pipe (medium class) | metre | 2 | 178.79 | 357.58
| Total cost of materials |  |  |  | 357.58
| Cartage @ 1 % of A1 |  |  |  | 3.5758
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.05 | 368 | 18.4
9999 | Sundries | L.S. | 20 | 1.1 | 22
| TOTAL |  |  |  | 421.9058
| OVERHEADS & PROFIT @ 15 % |  |  |  | 63.29
| Cost for 2 metres |  |  |  | 485.1958
| Rate per metre |  |  |  | 242.5979
| Say |  |  |  | 243
243
Analysis of rate
11.6 | Supplying and embedding following dia G.I. pipe (medium class) in pole collar/ foundation (during casting) for cable entry including bending the pipe to the required shape complete as required.
11.6.2 | 40 mm dia |  |  | DSR Rate Rs. | 276
Details of cost for 2 metre long 1 No pipe
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2826 | 40 mm dia. G.I. pipe (medium class) | metre | 2 | 207.95 | 415.9
| Total cost of materials |  |  |  | 415.9
| Cartage @ 1 % of A1 |  |  |  | 4.159
LABOUR
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.05 | 368 | 18.4
9999 | Sundries | L.S. | 20 | 1.1 | 22
| TOTAL |  |  |  | 480.809
| OVERHEADS & PROFIT @ 15 % |  |  |  | 72.12
| Cost for 2 metres |  |  |  | 552.929
| Rate per metre |  |  |  | 276.4645
| Say |  |  |  | 276
276
CHAPTER 12 – MV OVER HEAD LINE WORK (Analysis of rate based on DAR)
Analysis of rate
12.1 | Supplying and erection of stay set complete (galvanised) with 19/20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm, thimble, stay clamps, turn buckle ( 20 mm X 60 cm ), 7/ 4.00 mm dia G.I. stay wire and strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling etc. as required.
|  |  |  | DSR Rate Rs. | 3770
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2601 | Stay rod (1.8 M long, 19/20 mm dia.) with anchor plate 45 cm X 45 cm X 7.5 mm complete with thimble etc. | set | 1 | 540 | 540
2602 | Stay wire ( 7/4.00 mm dia.) | kg | 7.85 | 46.8 | 367.38
= 7.62 + 0.23 (wastage @ 3%) = 7.85 kg
2618 | Stay clamp | set | 1 | 63 | 63
2604 | Turn buckle ( 20 mm X 60 cm ) | each | 1 | 198 | 198
2605 | Strain insulator | each | 1 | 27 | 27
| Total cost of materials |  |  |  | 1195.38
| Cartage @ 1 % of A1 |  |  |  | 11.9538
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 1844.2838
| OVERHEADS & PROFIT @ 15 % |  |  |  | 276.64
| TOTAL |  |  |  | 2120.9238
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 3769.5238
| Rate per Each |  |  |  | 3769.5238
| Say |  |  |  | 3770
3770
Analysis of rate
12.2 | Supplying and erection of stay set complete (galvanised) with 19/20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm, thimble, stay clamps, turn buckle ( 20 mm X 60 cm ), 7/ 3.15 mm dia G.I. stay wire and strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling etc. as required.
|  |  |  | DSR Rate Rs. | 3624
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2601 | Stay rod (1.8 M long, 19/20 mm dia.) with anchor plate 45 cm X 45 cm X 7.5 mm complete with thimble etc. | set | 1 | 540 | 540
2603 | Stay wire ( 7/3.15 mm dia.) | kg | 5.17 | 46.8 | 241.96
= 4.92 + 0.25 (wastage @ 5%) = 5.17 kg
2618 | Stay clamp | set | 1 | 63 | 63
2604 | Turn buckle ( 20 mm X 60 cm ) | each | 1 | 198 | 198
2605 | Strain insulator | each | 1 | 27 | 27
| Total cost of materials |  |  |  | 1069.96
| Cartage @ 1 % of A1 |  |  |  | 10.6996
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 1717.6096
| OVERHEADS & PROFIT @ 15 % |  |  |  | 257.64
| TOTAL |  |  |  | 1975.2496
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 3623.8496
| Rate per Each |  |  |  | 3623.8496
| Say |  |  |  | 3624
3624
Analysis of rate
12.3 | Supplying and erection of stay set complete (galvanised) with 19/20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm, thimble, stay clamps, bow tightener, 7/ 4.00 mm dia G.I. stay wire and strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling etc. as required.
|  |  |  | DSR Rate Rs. | 3563
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2601 | Stay rod (1.8 M long, 19/20 mm dia.) with anchor plate 45 cm X 45 cm X 7.5 mm complete with thimble etc. | set | 1 | 540 | 540
2603 | Stay wire ( 7/3.15 mm dia.) | kg | 7.85 | 46.8 | 367.38
= 7.62 + 0.23 (wastage @ 3%) = 7.85 kg
2618 | Stay clamp | set | 1 | 63 | 63
2606 | Bow tightner | each | 1 | 19.8 | 19.8
2605 | Strain insulator | each | 1 | 27 | 27
| Total cost of materials |  |  |  | 1017.18
| Cartage @ 1 % of A1 |  |  |  | 10.1718
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 1664.3018
| OVERHEADS & PROFIT @ 15 % |  |  |  | 249.65
| TOTAL |  |  |  | 1913.9518
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 3562.5518
| Rate per Each |  |  |  | 3562.5518
| Say |  |  |  | 3563
3563
Analysis of rate
12.4 | Supplying and erection of stay set complete (galvanised) with 19/20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm, thimble, stay clamps, bow tightener, 7/ 3.15 mm dia G.I. stay wire and strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling etc. as required.
|  |  |  | DSR Rate Rs. | 3411
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2601 | Stay rod (1.8 M long, 19/20 mm dia.) with anchor plate 45 cm X 45 cm X 7.5 mm complete with thimble etc. | set | 1 | 540 | 540
2603 | Stay wire ( 7/3.15 mm dia.) | kg | 5.07 | 46.8 | 237.28
= 4.92 + 0.15 (Wastage @3%) = 5.07kg
2618 | Stay clamp | set | 1 | 63 | 63
2606 | Bow tightner | each | 1 | 19.8 | 19.8
2605 | Strain insulator | each | 1 | 27 | 27
| Total cost of materials |  |  |  | 887.08
| Cartage @ 1 % of A1 |  |  |  | 8.8708
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 1532.9008
| OVERHEADS & PROFIT @ 15 % |  |  |  | 229.94
| TOTAL |  |  |  | 1762.8408
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 3411.4408
| Rate per Each |  |  |  | 3411.4408
| Say |  |  |  | 3411
3411
Analysis of rate
12.5 | Supplying and erection of bow stay set complete (galvanised) with 19/20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm, thimble, stay clamps, turn buckle ( 20 mm X 60 cm ), 7/ 4.00 mm dia G.I. stay wire and strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling and also with 0.6 m long brace of size 50 mm X 50 mm X 6 mm angle iron with 50 mm dia pulley fixed at one end of the brace as required.
|  |  |  | DSR Rate Rs. | 4097
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2601 | Stay rod (1.8 M long, 19/20 mm dia.) with anchor plate 45 cm X 45 cm X 7.5 mm complete with thimble etc. | set | 1 | 540 | 540
2603 | Stay wire ( 7/3.15 mm dia.) | kg | 7.85 | 46.8 | 367.38
= 7.62 + 0.23 (wastage @ 3%) = 7.85 kg
2618 | Stay clamp | set | 2 | 63 | 126
2604 | Turn buckle ( 20 mm X 60 cm ) | each | 1 | 198 | 198
2605 | Strain insulator | each | 1 | 27 | 27
2619 | Brace ( 50 mm X 50 mm X 6 mm angle iron ) | metre | 0.6 | 211.5 | 126.9
2923 | Pulley of 50 mm dia | each | 1 | 72 | 72
| Total cost of materials |  |  |  | 1457.28
| Cartage @ 1 % of A1 |  |  |  | 14.5728
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 2129.1528
| OVERHEADS & PROFIT @ 15 % |  |  |  | 319.37
| TOTAL |  |  |  | 2448.5228
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 4097.1228
| Rate per Each |  |  |  | 4097.1228
| Say |  |  |  | 4097
4097
Analysis of rate
12.6 | Supplying and erection of bow stay set complete (galvanised) with 19/20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm, thimble, stay clamps, turn buckle ( 20 mm X 60 cm ), 7/ 3.15 mm dia G.I. stay wire and strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling and also with 0.6 m long brace of size 50 mm X 50 mm X 6 mm angle iron with 50 mm dia pulley fixed at one end of the brace as required.
|  |  |  | DSR Rate Rs. | 3946
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2601 | Stay rod (1.8 M long, 19/20 mm dia.) with anchor plate 45 cm X 45 cm X 7.5 mm complete with thimble etc. | set | 1 | 540 | 540
2603 | Stay wire ( 7/3.15 mm dia.) | kg | 5.07 | 46.8 | 237.28
= 4.92 + 0.15 (Wastage @3%) = 5.07kg
2618 | Stay clamp | set | 2 | 63 | 126
2604 | Turn buckle ( 20 mm X 60 cm ) | each | 1 | 198 | 198
2605 | Strain insulator | each | 1 | 27 | 27
2619 | Brace ( 50 mm X 50 mm X 6 mm angle iron ) | metre | 0.6 | 211.5 | 126.9
2923 | Pulley of 50 mm dia | each | 1 | 72 | 72
| Total cost of materials |  |  |  | 1327.18
| Cartage @ 1 % of A1 |  |  |  | 13.2718
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 1997.7518
| OVERHEADS & PROFIT @ 15 % |  |  |  | 299.66
| TOTAL |  |  |  | 2297.4118
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 3946.0118
| Rate per Each |  |  |  | 3946.0118
| Say |  |  |  | 3946
3946
Analysis of rate
12.7 | Supplying and erection of bow stay set complete (galvanised) with 19/20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm, thimble, stay clamps, bow tightener), 7/ 4.00 mm dia G.I. stay wire and strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling and also with 0.6 m long brace of size 50 mm X 50 mm X 6 mm angle iron with 50 mm dia pulley fixed at one end of the brace as required.
|  |  |  | DSR Rate Rs. | 3890
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2601 | Stay rod (1.8 M long, 19/20 mm dia.) with anchor plate 45 cm X 45 cm X 7.5 mm complete with thimble etc. | set | 1 | 540 | 540
2603 | Stay wire ( 7/3.15 mm dia.) | kg | 7.85 | 46.8 | 367.38
= 7.62 + 0.23 (wastage @ 3%) = 7.85 kg
2618 | Stay clamp | set | 2 | 63 | 126
2606 | Bow tightner | each | 1 | 19.8 | 19.8
2605 | Strain insulator | each | 1 | 27 | 27
2619 | Brace ( 50 mm X 50 mm X 6 mm angle iron ) | metre | 0.6 | 211.5 | 126.9
2923 | Pulley of 50 mm dia | each | 1 | 72 | 72
| Total cost of materials |  |  |  | 1279.08
| Cartage @ 1 % of A1 |  |  |  | 12.7908
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 1949.1708
| OVERHEADS & PROFIT @ 15 % |  |  |  | 292.38
| TOTAL |  |  |  | 2241.5508
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 3890.1508
| Rate per Each |  |  |  | 3890.1508
| Say |  |  |  | 3890
3890
Analysis of rate
12.8 | Supplying and erection of bow stay set complete (galvanised) with 19/20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm, thimble, stay clamps, bow tightener), 7/ 3.15mm dia G.I. stay wire and strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling and also with 0.6 m long brace of size 50 mm X 50 mm X 6 mm angle iron with 50 mm dia pulley fixed at one end of the brace as required.
|  |  |  | DSR Rate Rs. | 3739
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2601 | Stay rod (1.8 M long, 19/20 mm dia.) with anchor plate 45 cm X 45 cm X 7.5 mm complete with thimble etc. | set | 1 | 540 | 540
2603 | Stay wire ( 7/3.15 mm dia.) | kg | 5.07 | 46.8 | 237.28
= 4.92 + 0.15 (Wastage @3%) = 5.07kg
2618 | Stay clamp | set | 2 | 63 | 126
2606 | Bow tightner | each | 1 | 19.8 | 19.8
2605 | Strain insulator | each | 1 | 27 | 27
2619 | Brace ( 50 mm X 50 mm X 6 mm angle iron ) | metre | 0.6 | 211.5 | 126.9
2923 | Pulley of 50 mm dia | each | 1 | 72 | 72
| Total cost of materials |  |  |  | 1148.98
| Cartage @ 1 % of A1 |  |  |  | 11.4898
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 1817.7698
| OVERHEADS & PROFIT @ 15 % |  |  |  | 272.67
| TOTAL |  |  |  | 2090.4398
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 3739.0398
| Rate per Each |  |  |  | 3739.0398
| Say |  |  |  | 3739
3739
Analysis of rate
12.9 | Erection of stay set complete (galvanised) in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling etc. as required.
|  |  |  | DSR Rate Rs. | 2381
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 636.95
| OVERHEADS & PROFIT @ 15 % |  |  |  | 95.54
| TOTAL |  |  |  | 732.49
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 2381.09
| Rate per Each |  |  |  | 2381.09
| Say |  |  |  | 2381
2381
Analysis of rate
12.10 | Supplying of channel iron 75 mm X 40 mm X 6 mm (7.14 kg per metre) cross arm for 2 wire over head line complete with clamps, bolts, nuts and washer etc including drilling of holes for insulator pins etc (as per drawing) and painting with primer and finished paint as required .
|  |  |  | DSR Rate Rs. | 437
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2816 | 75 mm X 40 mm X 6 mm channel iron ( 7.14 kg/ mtr) | kg | 4.01 | 37.8 | 151.58
= 0.55mtr = 3.93kg + 0.08 (wastage @ 2%) = 4.01 kg
2813 | 50 mm X 6 mm flat iron | kg | 0.92 | 37.8 | 34.78
= 0.9 + 0.02 (wastage @ 2%) = 0.92 kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 2 | 6 | 12
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 202.36
| Cartage @ 1 % of A1 |  |  |  | 2.0236
LABOUR
1005 | Fitter, Grade 2 | day | 0.12 | 407 | 48.84
1009 | Blacksmith, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.18 | 368 | 66.24
1084 | Drilling holes | each | 6 | 6 | 36
| TOTAL |  |  |  | 379.8836
| OVERHEADS & PROFIT @ 15 % |  |  |  | 56.98
| TOTAL |  |  |  | 436.8636
| Rate per Set |  |  |  | 436.8636
| Say |  |  |  | 437
437
Analysis of rate
12.11 | Supplying of channel iron 75 mm X 40 mm X 6 mm (7.14 kg per metre) cross arm for 4 wire over head line complete with clamps, bolts, nuts and washer etc including drilling of holes for insulator pins etc (as per drawing) and painting with primer and finished paint as required .
|  |  |  | DSR Rate Rs. | 728
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2816 | 75 mm X 40 mm X 6 mm channel iron ( 7.14 kg/ mtr) | kg | 8.37 | 37.8 | 316.39
= 1.15 mtr = 8.21kg + 0.16 (wastage @ 2%) = 8.37 kg
2813 | 50 mm X 6 mm flat iron | kg | 0.92 | 37.8 | 34.78
= 0.9 + 0.02 (wastage @ 2%) = 0.92 kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 2 | 6 | 12
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 367.17
| Cartage @ 1 % of A1 |  |  |  | 3.6717
LABOUR
1005 | Fitter, Grade 2 | day | 0.21 | 407 | 85.47
1009 | Blacksmith, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.25 | 368 | 92
1084 | Drilling holes | each | 10 | 6 | 60
| TOTAL |  |  |  | 632.7317
| OVERHEADS & PROFIT @ 15 % |  |  |  | 94.91
| TOTAL |  |  |  | 727.6417
| Rate per Set |  |  |  | 727.6417
| Say |  |  |  | 728
728
Analysis of rate
12.12 | Erection of angle iron/ channel iron cross arm on wood/ RCC/ PCC/ steel tubular/ rail pole etc. as required.
|  |  |  | DSR Rate Rs. | 150
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.11 | 447 | 49.17
1007 | Khallasi | day | 0.22 | 368 | 80.96
| TOTAL |  |  |  | 130.13
| OVERHEADS & PROFIT @ 15 % |  |  |  | 19.52
| TOTAL |  |  |  | 149.65
| Rate per Set |  |  |  | 149.65
| Say |  |  |  | 150
150
Analysis of rate
12.13 | Supplying and erection of galvanised 'D' iron clamps complete with shackle insulator (75 mm X 90 mm),G. I. bolts, nuts and washers, coach screws etc. as required.
|  |  |  | DSR Rate Rs. | 204
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2635 | D' iron clamp (with coach screws) | each | 1 | 76.5 | 76.5
2607 | Shackle insulator ( 75 mm X 90 mm ) with G.I. bolts and nuts | set | 1 | 36.45 | 36.45
| Total cost of materials |  |  |  | 112.95
| Cartage @ 1 % of A1 |  |  |  | 1.1295
LABOUR
1003 | Lineman | day | 0.04 | 447 | 17.88
1005 | Fitter, Grade 2 | day | 0.04 | 407 | 16.28
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 177.6795
| OVERHEADS & PROFIT @ 15 % |  |  |  | 26.65
| TOTAL |  |  |  | 204.3295
| Rate per Set |  |  |  | 204.3295
| Say |  |  |  | 204
204
Analysis of rate
12.14 | Supplying and erection of galvanised 'D' iron clamps complete with shackle insulator (100 mm X 110 mm), G.I. bolts, nuts and washers, coach screws etc. as required.
|  |  |  | DSR Rate Rs. | 235
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2635 | D' iron clamp (with coach screws) | each | 1 | 76.5 | 76.5
2608 | Shackle insulator ( 100 mm X 110 mm ) with G.I. bolts and nuts | set | 1 | 63 | 63
| Total cost of materials |  |  |  | 139.5
| Cartage @ 1 % of A1 |  |  |  | 1.395
LABOUR
1003 | Lineman | day | 0.04 | 447 | 17.88
1005 | Fitter, Grade 2 | day | 0.04 | 407 | 16.28
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 204.495
| OVERHEADS & PROFIT @ 15 % |  |  |  | 30.67
| TOTAL |  |  |  | 235.165
| Rate per Set |  |  |  | 235.165
| Say |  |  |  | 235
235
Analysis of rate
12.15 | Erection of galvanised 'D' iron clamps and insulator on pole as required.
|  |  |  | DSR Rate Rs. | 37
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.04 | 368 | 14.72
| TOTAL |  |  |  | 32.6
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4.89
| TOTAL |  |  |  | 37.49
| Rate per Set |  |  |  | 37.49
| Say |  |  |  | 37
37
Analysis of rate
12.16 | Supplying and erection of 75 mm X 90 mm shackle insulator with G. I. Bolt, nuts and straps etc. as required.
|  |  |  | DSR Rate Rs. | 146
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2607 | Shackle insulator ( 75 mm X 90 mm ) with G.I. bolts and nuts | set | 1 | 36.45 | 36.45
2665 | G.I. strap for shackle insulator | set | 1 | 54 | 54
| Total cost of materials |  |  |  | 90.45
| Cartage @ 1 % of A1 |  |  |  | 0.9045
LABOUR
1003 | Lineman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 126.8445
| OVERHEADS & PROFIT @ 15 % |  |  |  | 19.03
| TOTAL |  |  |  | 145.8745
| Rate per Set |  |  |  | 145.8745
| Say |  |  |  | 146
146
Analysis of rate
12.17 | Supplying and erection of 100 mm X 110 mm shackle insulator with G. I. Bolt, nuts and straps etc. as required.
|  |  |  | DSR Rate Rs. | 177
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2608 | Shackle insulator ( 100 mm X 110 mm ) with G.I. bolts and nuts | set | 1 | 63 | 63
2665 | G.I. strap for shackle insulator | set | 1 | 54 | 54
| Total cost of materials |  |  |  | 117
| Cartage @ 1 % of A1 |  |  |  | 1.17
LABOUR
1003 | Lineman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 153.66
| OVERHEADS & PROFIT @ 15 % |  |  |  | 23.05
| TOTAL |  |  |  | 176.71
| Rate per Set |  |  |  | 176.71
| Say |  |  |  | 177
177
Analysis of rate
12.18 | Supplying and erection of 100 mm X 65 mm pin insulator complete with G. I. Spindle and nuts etc. as required.
|  |  |  | DSR Rate Rs. | 81
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2609 | Pin insulator ( 100 mm X 65 mm ) with G.I. spindle and nuts | set | 1 | 34.2 | 34.2
| Total cost of materials |  |  |  | 34.2
| Cartage @ 1 % of A1 |  |  |  | 0.342
LABOUR
1003 | Lineman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 70.032
| OVERHEADS & PROFIT @ 15 % |  |  |  | 10.5
| TOTAL |  |  |  | 80.532
| Rate per Set |  |  |  | 80.532
| Say |  |  |  | 81
81
Analysis of rate
12.19 | Supplying and erection of 100 mm X 80 mm pin insulator complete with G. I. Spindle and nuts etc. as required.
|  |  |  | DSR Rate Rs. | 83
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2610 | Pin insulator ( 100 mm X 80 mm ) with G.I. spindle and nuts | set | 1 | 36 | 36
| Total cost of materials |  |  |  | 36
| Cartage @ 1 % of A1 |  |  |  | 0.36
LABOUR
1003 | Lineman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 71.85
| OVERHEADS & PROFIT @ 15 % |  |  |  | 10.78
| TOTAL |  |  |  | 82.63
| Rate per Set |  |  |  | 82.63
| Say |  |  |  | 83
83
Analysis of rate
12.20 | Erection of LV/MV shackle/pin insulator etc. as required.
|  |  |  | DSR Rate Rs. | 41
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.03 | 447 | 13.41
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 35.49
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5.32
| TOTAL |  |  |  | 40.81
| Rate per Set |  |  |  | 40.81
| Say |  |  |  | 41
41
Analysis of rate
12.21 | Erection of ACSR conductor of 7/2.11 mm to 7/3.00 mm diameter including binding etc. as required.
|  |  |  | DSR Rate Rs. | 99
Details of cost for 133 kg
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 5 | 447 | 2235
1007 | Khallasi | day | 25 | 368 | 9200
| TOTAL |  |  |  | 11435
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1715.25
| Cost for 133 Kg |  |  |  | 13150.25
| Rate per Kg |  |  |  | 98.8741
| Say |  |  |  | 99
99
Analysis of rate
12.22 | Erection of ACSR conductor of 7/3.35 mm to 7/4.00 diameter and above including binding etc. as required.
|  |  |  | DSR Rate Rs. | 130
Details of cost for 133 kg
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 9 | 447 | 4023
1007 | Khallasi | day | 30 | 368 | 11040
| TOTAL |  |  |  | 15063
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2259.45
| Cost for 133 Kg |  |  |  | 17322.45
| Rate per Kg |  |  |  | 130.244
| Say |  |  |  | 130
130
Analysis of rate
12.23 | Erection of all aluminium conductor of 7/1.96 mm to 7/3.10 mm diameter including binding etc. as required.
|  |  |  | DSR Rate Rs. | 130
Details of cost for 101 kg
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 5 | 447 | 2235
1007 | Khallasi | day | 25 | 368 | 9200
| TOTAL |  |  |  | 11435
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1715.25
| Cost for 101 Kg |  |  |  | 13150.25
| Rate per Kg |  |  |  | 130.2005
| Say |  |  |  | 130
130
Analysis of rate
12.24 | Erection of all aluminium conductor of 7/3.40 mm to 7/4.00 mm diameter and above including binding etc. as required.
|  |  |  | DSR Rate Rs. | 100
Details of cost for 174 kg
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 9 | 447 | 4023
1007 | Khallasi | day | 30 | 368 | 11040
| TOTAL |  |  |  | 15063
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2259.45
| Cost for 174 Kg |  |  |  | 17322.45
| Rate per Kg |  |  |  | 99.5543
| Say |  |  |  | 100
100
Analysis of rate
12.25 | Erection of G.I. Wire No. 8 SWG including binding etc. as required.
|  |  |  | DSR Rate Rs. | 20
Details of cost for 153 kg
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 1.25 | 447 | 558.75
1007 | Khallasi | day | 5.62 | 368 | 2068.16
| TOTAL |  |  |  | 2626.91
| OVERHEADS & PROFIT @ 15 % |  |  |  | 394.04
| Cost for 153 Kg |  |  |  | 3020.95
| Rate per Kg |  |  |  | 19.7448
| Say |  |  |  | 20
20
Analysis of rate
12.26 | Erection of hexagonal type guard as required.
|  |  |  | DSR Rate Rs. | 107
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.06 | 447 | 26.82
1007 | Khallasi | day | 0.18 | 368 | 66.24
| TOTAL |  |  |  | 93.06
| OVERHEADS & PROFIT @ 15 % |  |  |  | 13.96
| TOTAL |  |  |  | 107.02
| Rate per Each |  |  |  | 107.02
| Say |  |  |  | 107
107
Analysis of rate
12.27 | Erection of ring type guard as required.
|  |  |  | DSR Rate Rs. | 36
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.02 | 447 | 8.94
1007 | Khallasi | day | 0.06 | 368 | 22.08
| TOTAL |  |  |  | 31.02
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4.65
| TOTAL |  |  |  | 35.67
| Rate per Each |  |  |  | 35.67
| Say |  |  |  | 36
36
Analysis of rate
12.28 | Erection of cradle guard as required.
|  |  |  | DSR Rate Rs. | 71
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 62.04
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9.31
| TOTAL |  |  |  | 71.35
| Rate per Each |  |  |  | 71.35
| Say |  |  |  | 71
71
Analysis of rate
12.29 | Supplying and erection of 15 A aerial fuse complete as required.
|  |  |  | DSR Rate Rs. | 73
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2615 | 15 amps aerial fuse complete with porcelain tube as required | each | 1 | 16.2 | 16.2
| Total cost of materials |  |  |  | 16.2
| Cartage @ 1 % of A1 |  |  |  | 0.162
LABOUR
1003 | Lineman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 63.682
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9.55
| TOTAL |  |  |  | 73.232
| Rate per Each |  |  |  | 73.232
| Say |  |  |  | 73
73
Analysis of rate
12.30 | Supplying and erection of 30 A aerial fuse complete as required.
|  |  |  | DSR Rate Rs. | 84
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2616 | 30 amps aerial fuse complete with porcelain tube as required | each | 1 | 25.2 | 25.2
| Total cost of materials |  |  |  | 25.2
| Cartage @ 1 % of A1 |  |  |  | 0.252
LABOUR
1003 | Lineman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 72.772
| OVERHEADS & PROFIT @ 15 % |  |  |  | 10.92
| TOTAL |  |  |  | 83.692
| Rate per Each |  |  |  | 83.692
| Say |  |  |  | 84
84
Analysis of rate
12.31 | Erection of aerial fuse as required.
|  |  |  | DSR Rate Rs. | 54
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.04 | 447 | 17.88
1007 | Khallasi | day | 0.08 | 368 | 29.44
| TOTAL |  |  |  | 47.32
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7.1
| TOTAL |  |  |  | 54.42
| Rate per Each |  |  |  | 54.42
| Say |  |  |  | 54
54
Analysis of rate
12.32 | Supplying and fixing MV horn gap lightning arrestor as required.
|  |  |  | DSR Rate Rs. | 197
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2611 | MV horn gap lightning arrestor with pin insulator ( 100 mm X 65 mm ), spindle and brass metal parts etc. | set | 1 | 99 | 99
| Total cost of materials |  |  |  | 99
| Cartage @ 1 % of A1 |  |  |  | 0.99
LABOUR
1003 | Lineman | day | 0.06 | 447 | 26.82
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 170.97
| OVERHEADS & PROFIT @ 15 % |  |  |  | 25.65
| TOTAL |  |  |  | 196.62
| Rate per Each |  |  |  | 196.62
| Say |  |  |  | 197
197
Analysis of rate
12.33 | Fixing of MV lightning arrestor as required.
|  |  |  | DSR Rate Rs. | 82
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.06 | 447 | 26.82
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 70.98
| OVERHEADS & PROFIT @ 15 % |  |  |  | 10.65
| TOTAL |  |  |  | 81.63
| Rate per Each |  |  |  | 81.63
| Say |  |  |  | 82
82
Analysis of rate
12.34 | Supplying and fixing of 32 mm dia X 2.00 metres long G.I. pipe (medium class) bracket for mounting of fluorescent / HPMV / HPSV street light fitting on pole including bending the pipe to the required shape, 2 nos 40 mm X 3 mm flat iron clamps with nuts, bolts and washer, painting the flat iron with primer and finish paint etc. as required.
|  |  |  | DSR Rate Rs. | 733
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2820 | 32 mm dia G.I. Pipe (light class) | metre | 2.04 | 152.25 | 310.59
= 2.0 + 0.04 (Wastage @ 2%) = 2.04m
2812 | 40 mm X 3 mm flat iron | kg | 2.65 | 37.8 | 100.17
= 2.6 + 0.05 (Wastage @ 2%) = 2.65kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 4 | 6 | 24
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 438.76
| Cartage @ 1 % of A1 |  |  |  | 4.3876
LABOUR
1005 | Fitter, Grade 2 | day | 0.12 | 407 | 48.84
1003 | Lineman | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 637.6276
| OVERHEADS & PROFIT @ 15 % |  |  |  | 95.64
| TOTAL |  |  |  | 733.2676
| Rate per Each |  |  |  | 733.2676
| Say |  |  |  | 733
733
Analysis of rate
12.35 | Providing and fixing 50 mm dia X 3.2 metres G.I. pipe (including accessories) complete with 50 mm X 50 mm X 6 mm angle iron bracket on wall and 75 mm X 90 mm shackle insulator with straps for house service connection including painting the angle and flat iron with primer and finish paint etc. as required.
|  |  |  | DSR Rate Rs. | 1727
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2821 | 50 mm dia G.I. Pipe (light class) | metre | 2.14 | 239 | 511.46
= 2.1 + 0.04 (Wastage @ 2%) = 2.14m
2839 | 50 mm dia. G.I. bend (medium class) | each | 3 | 90 | 270
2607 | Shackle insulator ( 75 mm X 90 mm ) with G.I. bolts and nuts | set | 2 | 36.45 | 72.9
2620 | Angle iron bracket ( 50 mm X 50 mm X 6 mm ) 65 cm long | each | 1 | 139.5 | 139.5
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2925 | Flat iron clamps (50 mm X 6 mm) for G.I. pipe | each | 4 | 28.9 | 115.6
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1133.46
| Cartage @ 1 % of A1 |  |  |  | 11.3346
LABOUR
1005 | Fitter, Grade 2 | day | 0.25 | 407 | 101.75
1003 | Lineman | day | 0.16 | 447 | 71.52
1007 | Khallasi | day | 0.5 | 368 | 184
| TOTAL |  |  |  | 1502.0646
| OVERHEADS & PROFIT @ 15 % |  |  |  | 225.31
| TOTAL |  |  |  | 1727.3746
| Rate per Each |  |  |  | 1727.3746
| Say |  |  |  | 1727
1727
Analysis of rate
12.36 | Providing and fixing 50 mm dia X 5.6 metres G.I. pipe (including accessories) complete with 50 mm X 50 mm X 6 mm angle iron cross arm and 40 mm X 3mm M.S. flat iron clamps bends for guard wire, 75 mm X 90 mm shackle insulator and straps, 7/ 3.15 mm G.I. wire stay set for house service connection including painting the angle and flat iron with primer and finish paint etc. as required.
|  |  |  | DSR Rate Rs. | 2593
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2821 | 50 mm dia G.I. Pipe (light class) | metre | 4.5 | 239 | 1075.5
= 4.5 + 0.09 (Wastage @ 2%) = 4.59m
2839 | 50 mm dia. G.I. bend (medium class) | each | 3 | 90 | 270
2807 | 50 mm X 50 mm X 6 mm angle iron | kg | 3.04 | 37.8 | 114.91
= 3.0 + 0.06 (Wastage @ 2%) = 3.06m
2607 | Shackle insulator ( 75 mm X 90 mm ) with G.I. bolts and nuts | set | 2 | 36.45 | 72.9
2855 | Steel fastener 6 mm X 75 mm | each | 4 | 5 | 20
2925 | Flat iron clamps (50 mm X 6 mm) for G.I. pipe | each | 4 | 28.9 | 115.6
2623 | Eye hook | each | 1 | 29.7 | 29.7
2603 | Stay wire ( 7/3.15 mm dia.) | kg | 0.82 | 46.8 | 38.38
= 3.0 + 0.06 (Wastage @ 2%) = 3.06m
2624 | Guy clamp | each | 1 | 67.5 | 67.5
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 2 | 6 | 12
2837 | Nipple 50 mm dia | each | 1 | 51.98 | 51.98
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1872.47
| Cartage @ 1 % of A1 |  |  |  | 18.7247
LABOUR
1005 | Fitter, Grade 2 | day | 0.16 | 407 | 65.12
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.41 | 368 | 150.88
| TOTAL |  |  |  | 2254.7047
| OVERHEADS & PROFIT @ 15 % |  |  |  | 338.21
| TOTAL |  |  |  | 2592.9147
| Rate per Each |  |  |  | 2592.9147
| Say |  |  |  | 2593
2593
Analysis of rate
12.37 | Supplying and fixing of light class G.I. pipe of 50 mm dia. (nominal) 3 metres length along the pole for protection of under ground cable as required.
|  |  |  | DSR Rate Rs. | 1217
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2821 | 50 mm dia G.I. Pipe (light class) | metre | 3.06 | 239 | 731.34
= 3.0 + 0.06 (Wastage @ 2%) = 3.06m
2812 | 40 mm X 3 mm flat iron | kg | 2.65 | 37.8 | 100.17
= 2.6 + 0.05 (Wastage @ 2%) = 2.65kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 4 | 6 | 24
| Total cost of materials |  |  |  | 855.51
| Cartage @ 1 % of A1 |  |  |  | 8.5551
LABOUR
1005 | Fitter, Grade 2 | day | 0.12 | 407 | 48.84
1003 | Lineman | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1058.5451
| OVERHEADS & PROFIT @ 15 % |  |  |  | 158.78
| TOTAL |  |  |  | 1217.3251
| Rate per Each |  |  |  | 1217.3251
| Say |  |  |  | 1217
1217
Analysis of rate
12.38 | Supplying and fixing of light class G.I. pipe of 80 mm dia. (nominal) 3 metres length along the pole for protection of under ground cable as required.
|  |  |  | DSR Rate Rs. | 1720
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2822 | 80 mm dia G.I. Pipe (light class) | metre | 3.06 | 380.36 | 1163.9
= 3.0 + 0.06 (Wastage @ 2%) = 3.06m
2812 | 40 mm X 3 mm flat iron | kg | 2.65 | 37.8 | 100.17
= 2.6 + 0.05 (Wastage @ 2%) = 2.65kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 4 | 6 | 24
| Total cost of materials |  |  |  | 1288.07
| Cartage @ 1 % of A1 |  |  |  | 12.8807
LABOUR
1005 | Fitter, Grade 2 | day | 0.12 | 407 | 48.84
1003 | Lineman | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1495.4307
| OVERHEADS & PROFIT @ 15 % |  |  |  | 224.31
| TOTAL |  |  |  | 1719.7407
| Rate per Each |  |  |  | 1719.7407
| Say |  |  |  | 1720
1720
Analysis of rate
12.39 | Supplying and fixing of light class G.I. pipe of 100 mm dia. (nominal) 3 metres length along the pole for protection of under ground cable as required.
|  |  |  | DSR Rate Rs. | 2256
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2823 | 100 mm dia G.I. Pipe (light class) | metre | 3.06 | 531.26 | 1625.66
= 3.0 + 0.06 (Wastage @ 2%) = 3.06m
2812 | 40 mm X 3 mm flat iron | kg | 2.65 | 37.8 | 100.17
= 2.6 + 0.05 (Wastage @ 2%) = 2.65kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 4 | 6 | 24
| Total cost of materials |  |  |  | 1749.83
| Cartage @ 1 % of A1 |  |  |  | 17.4983
LABOUR
1005 | Fitter, Grade 2 | day | 0.12 | 407 | 48.84
1003 | Lineman | day | 0.12 | 447 | 53.64
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 1961.8083
| OVERHEADS & PROFIT @ 15 % |  |  |  | 294.27
| TOTAL |  |  |  | 2256.0783
| Rate per Each |  |  |  | 2256.0783
| Say |  |  |  | 2256
2256
Analysis of rate
12.40 | Dismantling of over head lines comprising of copper/ aluminium over head conductor, G.I. wire, cross arms, insulators etc. as required.
|  |  |  | DSR Rate Rs. | 43
Details of cost for 64 Kg
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 2 | 447 | 894
1007 | Khallasi | day | 4 | 368 | 1472
| TOTAL |  |  |  | 2366
| OVERHEADS & PROFIT @ 15 % |  |  |  | 354.9
| Cost for 64 Kg |  |  |  | 2720.9
| Rate per Kg |  |  |  | 42.5141
| Say |  |  |  | 43
43
Analysis of rate
12.41 | Dismantling of pole/ street light standard/ strut embedded in brick ballast foundation etc. as required.
|  |  |  | DSR Rate Rs. | 975
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 2 | 368 | 736
| TOTAL |  |  |  | 847.75
| OVERHEADS & PROFIT @ 15 % |  |  |  | 127.16
| TOTAL |  |  |  | 974.91
| Rate per Each |  |  |  | 974.91
| Say |  |  |  | 975
975
Analysis of rate
12.42 | Dismantling of pole/ street light standard/ strut embedded in cement concrete foundation etc. as required.
|  |  |  | DSR Rate Rs. | 1295
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 2.66 | 368 | 978.88
| TOTAL |  |  |  | 1126.39
| OVERHEADS & PROFIT @ 15 % |  |  |  | 168.96
| TOTAL |  |  |  | 1295.35
| Rate per Each |  |  |  | 1295.35
| Say |  |  |  | 1295
1295
CHAPTER 13 – HV OVER HEAD LINE WORK (Analysis of rate based on DAR)
Analysis of rate
13.1 | Supplying and erection of galvanised stay set for 11 KV over head lines complete with 19/ 20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm thick, thimble, stay clamps, turn buckle ( 20 mm X 600 mm ), 7/ 4.00 mm dia G.I. stay wire and 11 KV strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling etc. as required.
|  |  |  | DSR Rate Rs. | 3808
Details of cost for one Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2601 | Stay rod (1.8 M long, 19/20 mm dia.) with anchor plate 45 cm X 45 cm X 7.5 mm complete with thimble etc. | set | 1 | 540 | 540
2602 | Stay wire ( 7/4.00 mm dia.) | kg | 8.65 | 46.8 | 404.82
= 8.40 + 0.25 (wastage @3%) = 8.65 kg
2618 | Stay clamp | set | 1 | 63 | 63
2604 | Turn buckle ( 20 mm X 60 cm ) | each | 1 | 198 | 198
2643 | Strain insulator 11 KV | each | 1 | 23 | 23
| Total cost of materials |  |  |  | 1228.82
| Cartage @ 1 % of A1 |  |  |  | 12.2882
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 1878.0582
| OVERHEADS & PROFIT @ 15 % |  |  |  | 281.71
| TOTAL |  |  |  | 2159.7682
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 3808.3682
| Rate per Set |  |  |  | 3808.3682
| Say |  |  |  | 3808
3808
Analysis of rate
13.2 | Supplying of channel iron 75 mm X 40 mm X 6 mm (7.14 kg per metre) pole top bracket/ cross arm for single 11 KV over head line conductor complete with 50 mm X 6mm flat iron clamp, bolts, nuts and washers including drilling holes for insulator pins, bolts and nuts etc and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 323
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2816 | 75 mm X 40 mm X 6 mm channel iron ( 7.14 kg/ mtr) | kg | 1.82 | 37.8 | 68.8
= 1.78 + 0.04 (Wastage @ 2%) = 1.82kg
2813 | 50 mm X 6 mm flat iron | kg | 0.84 | 37.8 | 31.75
= 0.82 + 0.02 (Wastage @ 2%) = 0.84kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 2 | 6 | 12
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 116.55
| Cartage @ 1 % of A1 |  |  |  | 1.1655
LABOUR
1005 | Fitter, Grade 2 | day | 0.12 | 407 | 48.84
1009 | Blacksmith, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.18 | 368 | 66.24
1084 | Drilling holes | each | 4 | 6 | 24
| TOTAL |  |  |  | 281.2155
| OVERHEADS & PROFIT @ 15 % |  |  |  | 42.18
| TOTAL |  |  |  | 323.3955
| Rate per Each |  |  |  | 323.3955
| Say |  |  |  | 323
323
Analysis of rate
13.3 | Supplying of 50 mm X 8 mm M.S. flat iron pole top bracket/ cross arm for single 11/22/33 KV over head line conductor complete with fixing clamps, bolts, nuts and washers drilling holes for insulator pins, bolts and nuts etc and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 368
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2814 | 50 mm X 8 mm flat iron | kg | 1.63 | 37.8 | 61.61
= 1.60 + 0.03 (Wastage @ 2%) = 1.63kg
2869 | 16 mm X 125 mm bolts and nuts with washers | set | 2 | 20 | 40
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 105.61
| Cartage @ 1 % of A1 |  |  |  | 1.0561
LABOUR
1005 | Fitter, Grade 2 | day | 0.12 | 407 | 48.84
1009 | Blacksmith, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.18 | 368 | 66.24
1084 | Drilling holes | each | 4 | 6 | 24
1086 | Welding charges | mm | 100 | 0.5 | 50
| TOTAL |  |  |  | 320.1661
| OVERHEADS & PROFIT @ 15 % |  |  |  | 48.02
| TOTAL |  |  |  | 368.1861
| Rate per Each |  |  |  | 368.1861
| Say |  |  |  | 368
368
Analysis of rate
13.4 | Supplying of channel iron 75 mm X 40 mm X 6 mm (7.14 kg per metre) cross arm for two 11 KV over head line conductors complete with 50 mm X 50 mm X 6 mm (angle iron bracket welded to the channel iron and complete with 50 mm X 6mm M.S. flat iron clamps, bolts and nuts including drilling holes for insulator pins, bolts, nuts and washers etc (as per drawing) and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 1358
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2816 | 75 mm X 40 mm X 6 mm channel iron ( 7.14 kg/ mtr) | kg | 8.01 | 37.8 | 302.78
= 7.85 + 0.16 (Wastage @ 2%) = 8.01kg
2807 | 50 mm X 50 mm X 6 mm angle iron | kg | 8.52 | 37.8 | 322.06
= 8.35 + 0.17 (Wastage @ 2%) = 8.52kg
2813 | 50 mm X 6 mm flat iron | kg | 1.66 | 37.8 | 62.75
= 1.63 + 0.03 (Wastage @ 2%) = 1.66kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 4 | 6 | 24
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 715.59
| Cartage @ 1 % of A1 |  |  |  | 7.1559
LABOUR
1005 | Fitter, Grade 2 | day | 0.25 | 407 | 101.75
1009 | Blacksmith, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.4 | 368 | 147.2
1086 | Welding charges | mm | 200 | 0.5 | 100
1084 | Drilling holes | each | 8 | 6 | 48
| TOTAL |  |  |  | 1180.7459
| OVERHEADS & PROFIT @ 15 % |  |  |  | 177.11
| TOTAL |  |  |  | 1357.8559
| Rate per Each |  |  |  | 1357.8559
| Say |  |  |  | 1358
1358
Analysis of rate
13.5 | Supplying of channel iron 75 mm X 40 mm X 6 mm (7.14 kg per metre) V shape cross arm for two 11 KV over head line conductors complete with 50 mm X 6mm M.S. flat iron clamps, bolts and nuts including drilling holes for insulator pins, bolts, nuts and washers etc (as per drawing) and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 1163
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2816 | 75 mm X 40 mm X 6 mm channel iron ( 7.14 kg/ mtr) | kg | 10.25 | 37.8 | 387.45
= 10.05 + 0.201 (Wastage @ 2%) = 10.251kg
2813 | 50 mm X 6 mm flat iron | kg | 0.84 | 37.8 | 31.75
= 0.82 + 0.02 (Wastage @ 2%) = 0.84kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 2 | 6 | 12
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 435.2
| Cartage @ 1 % of A1 |  |  |  | 4.352
LABOUR
1005 | Fitter, Grade 2 | day | 0.3 | 407 | 122.1
1009 | Blacksmith, Grade 2 | day | 0.2 | 407 | 81.4
1007 | Khallasi | day | 0.5 | 368 | 184
1086 | Welding charges | mm | 320 | 0.5 | 160
1084 | Drilling holes | each | 4 | 6 | 24
| TOTAL |  |  |  | 1011.052
| OVERHEADS & PROFIT @ 15 % |  |  |  | 151.66
| TOTAL |  |  |  | 1162.712
| Rate per Each |  |  |  | 1162.712
| Say |  |  |  | 1163
1163
Analysis of rate
13.6 | Erection of pole top/ straight two wire/ V shape two wire, angle iron/ channel iron, cross arm on steel tubular/ rail/ PCC pole for 11/22/33 KV as required.
|  |  |  | DSR Rate Rs. | 272
Details of cost for One Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 236.6
| OVERHEADS & PROFIT @ 15 % |  |  |  | 35.49
| TOTAL |  |  |  | 272.09
| Rate per Set |  |  |  | 272.09
| Say |  |  |  | 272
272
Analysis of rate
13.7 | Supplying of two lengths of channel iron 75 mm X 40 mm X 6 mm (7.14 kg per metre) double pole cross arm for three wire 11KV over head line conductors complete with through bolts and nuts for clamping to the poles, 50 mm X 6 mm M.S. flats welded on one side to the channel iron and with bolts and nuts on the other side for tying the cross arms together, including drilling holes for insulator pins/ fittings, bolts, nuts and washers etc (as per drawing) and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 2925
Details of cost for One Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2816 | 75 mm X 40 mm X 6 mm channel iron ( 7.14 kg/ mtr) | kg | 33.5 | 37.8 | 1266.3
= 32.84 + 0.66 (Wastage @ 2%) = 33.50kg
2813 | 50 mm X 6 mm flat iron | kg | 2.57 | 37.8 | 97.15
= 2.52 + 0.0504 (Wastage @ 2%) = 2.57kg
2869 | 16 mm X 125 mm bolts and nuts with washers | set | 4 | 20 | 80
2868 | 16 mm X 40 mm bolts and nuts with washers | set | 12 | 6 | 72
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1519.45
| Cartage @ 1 % of A1 |  |  |  | 15.1945
LABOUR
1005 | Fitter, Grade 2 | day | 0.5 | 407 | 203.5
1009 | Blacksmith, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 1.5 | 368 | 552
1084 | Drilling holes | each | 32 | 6 | 192
| TOTAL |  |  |  | 2543.1945
| OVERHEADS & PROFIT @ 15 % |  |  |  | 381.48
| TOTAL |  |  |  | 2924.6745
| Rate per Set |  |  |  | 2924.6745
| Say |  |  |  | 2925
2925
Analysis of rate
13.8 | Supplying and erection of a set of cross bracing frame work for 11 KV over head line double pole structure having four members fabricated out of 50 mm X 50 mm X 6 mm angle iron to form a rectangle of minimum size 1400 mm width X 2500 mm height, complete with 50 mm X 6mm M.S. flat iron clamps, bolts and nuts including drilling holes for insulator pins, bolts and nuts etc (as per drawing) and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 4230
Details of cost for One Set
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2807 | 50 mm X 50 mm X 6 mm angle iron | kg | 42.82 | 37.8 | 1618.6
= 41.98 + 0.84 (Wastage @ 2%) = 42.82kg
2813 | 50 mm X 6 mm flat iron | kg | 3.72 | 37.8 | 140.62
= 3.65 + 0.07 (Wastage @ 2%) = 3.72kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 8 | 6 | 48
2868 | 16 mm X 40 mm bolts and nuts with washers | set | 1 | 6 | 6
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1817.22
| Cartage @ 1 % of A1 |  |  |  | 18.1722
LABOUR
1003 | Lineman | day | 0.5 | 447 | 223.5
1005 | Fitter, Grade 2 | day | 0.5 | 407 | 203.5
1009 | Blacksmith, Grade 2 | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 3 | 368 | 1104
1084 | Drilling holes | each | 18 | 6 | 108
| TOTAL |  |  |  | 3677.8922
| OVERHEADS & PROFIT @ 15 % |  |  |  | 551.68
| TOTAL |  |  |  | 4229.5722
| Rate per Set |  |  |  | 4229.5722
| Say |  |  |  | 4230
4230
Analysis of rate
13.9 | Erection of double pole 3 wire cross arm for 11KV/ 22KV/ 33 KV over head lines as required.
|  |  |  | DSR Rate Rs. | 624
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.35 | 447 | 156.45
1007 | Khallasi | day | 1.05 | 368 | 386.4
| TOTAL |  |  |  | 542.85
| OVERHEADS & PROFIT @ 15 % |  |  |  | 81.43
| TOTAL |  |  |  | 624.28
| Rate per Each |  |  |  | 624.28
| Say |  |  |  | 624
624
Analysis of rate
13.10 | Supplying and erection of 11 KV pin insulator complete with large steel head G.I. pin, nuts, washers etc. as required.
|  |  |  | DSR Rate Rs. | 225
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2645 | 11 KV pin insulator with pin washers and nuts | set | 1 | 113 | 113
| Total cost of materials |  |  |  | 113
| Cartage @ 1 % of A1 |  |  |  | 1.13
LABOUR
1003 | Lineman | day | 0.1 | 447 | 44.7
1007 | Khallasi | day | 0.1 | 368 | 36.8
| TOTAL |  |  |  | 195.63
| OVERHEADS & PROFIT @ 15 % |  |  |  | 29.34
| TOTAL |  |  |  | 224.97
| Rate per Each |  |  |  | 224.97
| Say |  |  |  | 225
225
Analysis of rate
13.11 | Supplying and erection of 11 KV disc insulator for 11 KV over head lines with galvanised insulator fittings, ball and socket type and complete with galvanised strain clamps, bolts, nuts, washers etc. as required.
|  |  |  | DSR Rate Rs. | 898
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2646 | 11 KV disc insulator | set | 1 | 506 | 506
2647 | Galvanised insulator hardware fitting ball and socket type with strain clamps, bolts, nuts and washers | set | 1 | 148.5 | 148.5
| Total cost of materials |  |  |  | 654.5
| Cartage @ 1 % of A1 |  |  |  | 6.545
LABOUR
1003 | Lineman | day | 0.1 | 447 | 44.7
1005 | Fitter, Grade 2 | day | 0.05 | 407 | 20.35
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 781.295
| OVERHEADS & PROFIT @ 15 % |  |  |  | 117.19
| TOTAL |  |  |  | 898.485
| Rate per Each |  |  |  | 898.485
| Say |  |  |  | 898
898
Analysis of rate
13.12 | Erection of disc/ pin insulator for 11 KV over head lines as required.
|  |  |  | DSR Rate Rs. | 82
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1003 | Lineman | day | 0.06 | 447 | 26.82
1007 | Khallasi | day | 0.12 | 368 | 44.16
| TOTAL |  |  |  | 70.98
| OVERHEADS & PROFIT @ 15 % |  |  |  | 10.65
| TOTAL |  |  |  | 81.63
| Rate per Set |  |  |  | 81.63
| Say |  |  |  | 82
82
Analysis of rate
13.13 | Supplying and erection of three piece nonlinear resistor type lightning arrestor suitable for 3 wire, 11 KV overhead lines with rated voltage 9 KV (rms) with a nominal discharge current rating of 5 KA and complete with galvanised clamping arrangement, G.I. bolts, nuts, washers etc. as required.
|  |  |  | DSR Rate Rs. | 2325
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2650 | 3 piece lightning arrestor set for 11 KV O.H. lines complete with G.I. clamps bolts and nuts with washers | set | 1 | 1800 | 1800
| Total cost of materials |  |  |  | 1800
| Cartage @ 1 % of A1 |  |  |  | 18
LABOUR
1003 | Lineman | day | 0.25 | 447 | 111.75
1007 | Khallasi | day | 0.25 | 368 | 92
| TOTAL |  |  |  | 2021.75
| OVERHEADS & PROFIT @ 15 % |  |  |  | 303.26
| TOTAL |  |  |  | 2325.01
| Rate per Each |  |  |  | 2325.01
| Say |  |  |  | 2325
2325
Analysis of rate
13.14 | Supplying and erection of galvanised stay set for 33 KV over head lines complete with 19/ 20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm thick, thimble, stay clamps, turn buckle ( 20 mm X 600 mm ), 7/ 4.00 mm dia G.I. stay wire and 33 KV strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling etc. as required.
|  |  |  | DSR Rate Rs. | 3821
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2601 | Stay rod (1.8 M long, 19/20 mm dia.) with anchor plate 45 cm X 45 cm X 7.5 mm complete with thimble etc. | set | 1 | 540 | 540
2602 | Stay wire ( 7/4.00 mm dia.) | kg | 8.65 | 46.8 | 404.82
= 8.40 + 0.25 (wastage @ 3%) = 8.65 kg
2618 | Stay clamp | set | 1 | 63 | 63
2604 | Turn buckle ( 20 mm X 60 cm ) | each | 1 | 198 | 198
2644 | Strain insulator 33 KV | each | 1 | 34 | 34
| Total cost of materials |  |  |  | 1239.82
| Cartage @ 1 % of A1 |  |  |  | 12.3982
LABOUR
1003 | Lineman | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 1.33 | 368 | 489.44
| TOTAL |  |  |  | 1889.1682
| OVERHEADS & PROFIT @ 15 % |  |  |  | 283.38
| TOTAL |  |  |  | 2172.5482
14.4 | Excavation including refilling as required | cum | 1.2 | 318 | 381.6
14.9 | Cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) | cum | 0.28 | 4525 | 1267
| TOTAL |  |  |  | 3821.1482
| Rate per Each |  |  |  | 3821.1482
| Say |  |  |  | 3821
3821
Analysis of rate
13.15 | Supplying of channel iron 75 mm X 40 mm X 6 mm (7.14 kg per metre) pole top bracket/ cross arm for single 33 KV over head line conductor complete with 50 mm X 6mm flat iron clamps, bolts and nuts including drilling holes for insulator pins, bolts, nuts, washers etc and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 339
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2816 | 75 mm X 40 mm X 6 mm channel iron ( 7.14 kg/ mtr) | kg | 2.18 | 37.8 | 82.4
= 1.15 mtr = 8.21kg + 0.16 (wastage @ 2%) = 8.37 kg
2813 | 50 mm X 6 mm flat iron | kg | 0.84 | 37.8 | 31.75
= 0.82 + 0.02 (Wastage @ 2%) = 0.84kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 2 | 6 | 12
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 130.15
| Cartage @ 1 % of A1 |  |  |  | 1.3015
LABOUR
1005 | Fitter, Grade 2 | day | 0.12 | 407 | 48.84
1009 | Blacksmith, Grade 2 | day | 0.06 | 407 | 24.42
1007 | Khallasi | day | 0.18 | 368 | 66.24
1084 | Drilling holes | each | 4 | 6 | 24
| TOTAL |  |  |  | 294.9515
| OVERHEADS & PROFIT @ 15 % |  |  |  | 44.24
| TOTAL |  |  |  | 339.1915
| Rate per Each |  |  |  | 339.1915
| Say |  |  |  | 339
339
Analysis of rate
13.16 | Supplying of channel iron 75 mm X 40 mm X 6 mm (7.14 kg per metre) cross arm for two 33 KV over head line conductors complete with 50 mm X 50 mm X 6 mm angle iron bracket welded to the channel iron and complete with 50 mm X 6mm M.S. flat iron clamps, bolts and nuts including drilling holes for insulator pins, bolts, nuts, washers etc and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 1670
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2816 | 75 mm X 40 mm X 6 mm channel iron ( 7.14 kg/ mtr) | kg | 11.65 | 37.8 | 440.37
= 11.42 + 0.23 (Wastage @ 2%) = 11.65kg
2807 | 50 mm X 50 mm X 6 mm angle iron | kg | 11.99 | 37.8 | 453.22
= 11.75 + 0.24 (Wastage @ 2%) = 11.99kg
2813 | 50 mm X 6 mm flat iron | kg | 1.66 | 37.8 | 62.75
= 1.63 + 0.03 (Wastage @ 2%) = 1.66kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 4 | 6 | 24
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 984.34
| Cartage @ 1 % of A1 |  |  |  | 9.8434
LABOUR
1005 | Fitter, Grade 2 | day | 0.25 | 407 | 101.75
1009 | Blacksmith, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.4 | 368 | 147.2
1084 | Drilling holes | each | 8 | 6 | 48
1086 | Welding charges | mm | 200 | 0.5 | 100
| TOTAL |  |  |  | 1452.1834
| OVERHEADS & PROFIT @ 15 % |  |  |  | 217.83
| TOTAL |  |  |  | 1670.0134
| Rate per Each |  |  |  | 1670.0134
| Say |  |  |  | 1670
1670
Analysis of rate
13.17 | Supplying of channel iron 75 mm X 40 mm X 6 mm (7.14 kg per metre) V shape cross arm for two 33 KV over head line conductors complete with 50 mm X 6mm M.S. flat iron clamps, bolts and nuts including drilling holes for insulator pins, bolts and nuts etc and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 1307
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2816 | 75 mm X 40 mm X 6 mm channel iron ( 7.14 kg/ mtr) | kg | 13.53 | 37.8 | 511.43
= 13.26 + 0.27 (Wastage @ 2%) = 13.53kg
2813 | 50 mm X 6 mm flat iron | kg | 0.84 | 37.8 | 31.75
= 0.82 + 0.02 (Wastage @ 2%) = 0.84kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 2 | 6 | 12
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 559.18
| Cartage @ 1 % of A1 |  |  |  | 5.5918
LABOUR
1005 | Fitter, Grade 2 | day | 0.3 | 407 | 122.1
1009 | Blacksmith, Grade 2 | day | 0.2 | 407 | 81.4
1007 | Khallasi | day | 0.5 | 368 | 184
1086 | Welding charges | mm | 320 | 0.5 | 160
1084 | Drilling holes | each | 4 | 6 | 24
| TOTAL |  |  |  | 1136.2718
| OVERHEADS & PROFIT @ 15 % |  |  |  | 170.44
| TOTAL |  |  |  | 1306.7118
| Rate per Each |  |  |  | 1306.7118
| Say |  |  |  | 1307
1307
Analysis of rate
13.18 | Supplying of channel iron 100 mm X 50 mm X 6 mm (9.56 kg per metre), pole top bracket/ cross arm for single 33 KV over head line conductor complete with 50 mm X 6 mm M.S. flat iron clamps, bolts and nuts including drilling holes for insulator pins, bolts and nuts etc and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 416
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2815 | 100 mm X 50 mm X 6 mm channel iron ( 9.56 kg/ mtr) | kg | 2.93 | 37.8 | 110.75
= 2.87 + 0.06 (Wastage @ 2%) = 2.93kg
2813 | 50 mm X 6 mm flat iron | kg | 1.02 | 37.8 | 38.56
= 1.00 + 0.02 (Wastage @ 2%) = 1.02kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 2 | 6 | 12
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 165.31
| Cartage @ 1 % of A1 |  |  |  | 1.6531
LABOUR
1005 | Fitter, Grade 2 | day | 0.15 | 407 | 61.05
1009 | Blacksmith, Grade 2 | day | 0.07 | 407 | 28.49
1007 | Khallasi | day | 0.22 | 368 | 80.96
1084 | Drilling holes | each | 4 | 6 | 24
| TOTAL |  |  |  | 361.4631
| OVERHEADS & PROFIT @ 15 % |  |  |  | 54.22
| TOTAL |  |  |  | 415.6831
| Rate per Each |  |  |  | 415.6831
| Say |  |  |  | 416
416
Analysis of rate
13.19 | Supplying of channel iron 100 mm X 50 mm X 6 mm (9.56 kg per metre) cross arm for two wire 33 KV over head line conductors complete with 50 mm X 50 mm X 6 mm angle iron bracket welded to the channel iron and complete with 50 mm X 6mm M.S. flat iron clamps, bolts and nuts including drilling holes for insulator pins/ fittings, bolts, nuts, washers etc and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 2060
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2815 | 100 mm X 50 mm X 6 mm channel iron ( 9.56 kg/ mtr) | kg | 18.11 | 37.8 | 684.56
= 17.75 + 0.36 (Wastage @ 2%) = 18.11kg
2807 | 50 mm X 50 mm X 6 mm angle iron | kg | 11.99 | 37.8 | 453.22
= 11.75 + 0.24 (Wastage @ 2%) = 11.99kg
2813 | 50 mm X 6 mm flat iron | kg | 2.05 | 37.8 | 77.49
= 2.01 + 0.0402 (Wastage @ 2%) = 2.05kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 4 | 6 | 24
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1243.27
| Cartage @ 1 % of A1 |  |  |  | 12.4327
LABOUR
1005 | Fitter, Grade 2 | day | 0.35 | 407 | 142.45
1009 | Blacksmith, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.5 | 368 | 184
1086 | Welding charges | mm | 200 | 0.5 | 100
1084 | Drilling holes | each | 8 | 6 | 48
| TOTAL |  |  |  | 1791.2027
| OVERHEADS & PROFIT @ 15 % |  |  |  | 268.68
| TOTAL |  |  |  | 2059.8827
| Rate per Each |  |  |  | 2059.8827
| Say |  |  |  | 2060
2060
Analysis of rate
13.20 | Supplying of channel iron 100 mm X 50 mm X 6 mm (9.56 kg per metre) V shape cross arm for two 33 KV over head line conductors complete with 50 mm X 6mm M.S. flat iron clamps, bolts and nuts including drilling holes for insulator pins, bolts, nuts, washers etc and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 1611
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2815 | 100 mm X 50 mm X 6 mm channel iron ( 9.56 kg/ mtr) | kg | 18.11 | 37.8 | 684.56
= 17.75 + 0.36 (Wastage @ 2%) = 18.11kg
2813 | 50 mm X 6 mm flat iron | kg | 0.84 | 37.8 | 31.75
= 0.82 + 0.02 (Wastage @ 2%) = 0.84kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 2 | 6 | 12
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 732.31
| Cartage @ 1 % of A1 |  |  |  | 7.3231
LABOUR
1005 | Fitter, Grade 2 | day | 0.3 | 407 | 122.1
1009 | Blacksmith, Grade 2 | day | 0.2 | 407 | 81.4
1007 | Khallasi | day | 0.5 | 368 | 184
1086 | Welding charges | mm | 500 | 0.5 | 250
1084 | Drilling holes | each | 4 | 6 | 24
| TOTAL |  |  |  | 1401.1331
| OVERHEADS & PROFIT @ 15 % |  |  |  | 210.17
| TOTAL |  |  |  | 1611.3031
| Rate per Each |  |  |  | 1611.3031
| Say |  |  |  | 1611
1611
Analysis of rate
13.21 | Supplying of two lengths of channel iron 100 mm X 50 mm X 6 mm (9.56 kg per metre) double pole cross arm for three wire 33 KV over head line conductors complete with through bolts and nuts for clamping to the poles, 50 mm X 6 mm M.S. flats welded on one side to the channel iron and with bolts and nuts on the other side for tying the cross arms together, including drilling holes for insulator pins/ fittings, bolts, nuts, washers etc and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 4013
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2815 | 100 mm X 50 mm X 6 mm channel iron ( 9.56 kg/ mtr) | kg | 44.86 | 37.8 | 1695.71
= 43.98 + 0.8796 (Wastage @ 2%) = 44.86kg
2813 | 50 mm X 6 mm flat iron | kg | 2.94 | 37.8 | 111.13
= 2.88 + 0.06 (Wastage @ 2%) = 2.94kg
2870 | 16 mm X 150 mm bolts and nuts with washers | set | 4 | 24 | 96
2868 | 16 mm X 40 mm bolts and nuts with washers | set | 12 | 6 | 72
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 1978.84
| Cartage @ 1 % of A1 |  |  |  | 19.7884
LABOUR
1005 | Fitter, Grade 2 | day | 0.6 | 407 | 244.2
1009 | Blacksmith, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 2.7 | 368 | 993.6
1084 | Drilling holes | each | 32 | 6 | 192
| TOTAL |  |  |  | 3489.4784
| OVERHEADS & PROFIT @ 15 % |  |  |  | 523.42
| TOTAL |  |  |  | 4012.8984
| Rate per Each |  |  |  | 4012.8984
| Say |  |  |  | 4013
4013
Analysis of rate
13.22 | Supplying and erection of a set of cross bracing frame work for 33 KV over head line double pole structure having four members fabricated out of 65 mm X 65 mm X 6 mm angle iron to form a rectangle of minimum size 2400 mm width X 2800 mm height complete with 50 mm X 6mm M.S. flat iron clamps, bolts and nuts including drilling holes for insulator pins, bolts, nuts, washers etc and painting with primer and finish paint as required.
|  |  |  | DSR Rate Rs. | 6027
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2808 | 65 mm X 65 mm X 6 mm angle iron | kg | 77.95 | 37.8 | 2946.51
= 76.42 + 1.53 (Wastage @ 2%) = 77.95kg
2813 | 50 mm X 6 mm flat iron | kg | 4.51 | 37.8 | 170.48
= 4.42 + 0.09 (Wastage @ 2%) = 4.51kg
2867 | 16 mm X 50 mm bolts and nuts with washers | set | 8 | 6 | 48
2868 | 16 mm X 40 mm bolts and nuts with washers | set | 1 | 6 | 6
2936 | Painting with primer and finish paint | L.S. | 1 | 4 | 4
| Total cost of materials |  |  |  | 3174.99
| Cartage @ 1 % of A1 |  |  |  | 31.7499
LABOUR
1003 | Lineman | day | 0.6 | 447 | 268.2
1005 | Fitter, Grade 2 | day | 0.5 | 407 | 203.5
1009 | Blacksmith, Grade 2 | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 3.4 | 368 | 1251.2
1084 | Drilling holes | each | 18 | 6 | 108
| TOTAL |  |  |  | 5241.1399
| OVERHEADS & PROFIT @ 15 % |  |  |  | 786.17
| TOTAL |  |  |  | 6027.3099
| Rate per Each |  |  |  | 6027.3099
| Say |  |  |  | 6027
6027
Analysis of rate
13.23 | Supplying and erection of 33 KV pin insulator complete with large steel head G.I. pin, nuts, washers etc. as required.
|  |  |  | DSR Rate Rs. | 728
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2648 | 33 KV pin insulator with pin washers and nuts | set | 1 | 506 | 506
| Total cost of materials |  |  |  | 506
| Cartage @ 1 % of A1 |  |  |  | 5.06
LABOUR
1003 | Lineman | day | 0.15 | 447 | 67.05
1007 | Khallasi | day | 0.15 | 368 | 55.2
| TOTAL |  |  |  | 633.31
| OVERHEADS & PROFIT @ 15 % |  |  |  | 95
| TOTAL |  |  |  | 728.31
| Rate per Each |  |  |  | 728.31
| Say |  |  |  | 728
728
Analysis of rate
13.24 | Supplying and erection of a set of three 11 KV disc insulator for 33 KV over head lines with galvanised insulator fittings, ball and socket type and complete with galvanised strain clamps, bolts, nuts, washers etc. as required.
|  |  |  | DSR Rate Rs. | 2635
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2646 | 11 KV disc insulator | set | 3 | 506 | 1518
2649 | Galvanised insulator hardware fitting ball and socket type with strain clamps, bolts, nuts and washers for 3 Nos 11 KV disk insulator | set | 1 | 433.8 | 433.8
| Total cost of materials |  |  |  | 1951.8
| Cartage @ 1 % of A1 |  |  |  | 19.518
LABOUR
1003 | Lineman | day | 0.25 | 447 | 111.75
1005 | Fitter, Grade 2 | day | 0.15 | 407 | 61.05
1007 | Khallasi | day | 0.4 | 368 | 147.2
| TOTAL |  |  |  | 2291.318
| OVERHEADS & PROFIT @ 15 % |  |  |  | 343.7
| TOTAL |  |  |  | 2635.018
| Rate per Each |  |  |  | 2635.018
| Say |  |  |  | 2635
2635
Analysis of rate
13.25 | Supplying and erection of single piece nonlinear resistor type lightning arrestor suitable for 3 wire, 33 KV overhead lines with rated voltage 30 KV (rms) with a nominal discharge current rating of 10 KA (station class) and complete with galvanised clamping arrangement, G.I. bolts, nuts, washers etc. as required.
|  |  |  | DSR Rate Rs. | 18575
Details of cost for one No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2651 | Single piece lightning arrestor set for 33 KV O.H. lines complete with G.I. clamps bolts and nuts with washers | set | 1 | 15750 | 15750
| Total cost of materials |  |  |  | 15750
| Cartage @ 1 % of A1 |  |  |  | 157.5
LABOUR
1003 | Lineman | day | 0.3 | 447 | 134.1
1007 | Khallasi | day | 0.3 | 368 | 110.4
| TOTAL |  |  |  | 16152
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2422.8
| TOTAL |  |  |  | 18574.8
| Rate per Each |  |  |  | 18574.8
| Say |  |  |  | 18575
18575
CHAPTER 14 – CIVIL ITEMS (Analysis of rate based on DAR)
Analysis of rate
14.1 | Excavation for foundation in soft soil including dressing of sides and ramming of bottoms, lift upto 1.5 m including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 metres.
|  |  |  | DSR Rate Rs. | 192
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1016 | Mate | day | 0.25 | 368 | 92
1012 | Beldar/ coolie | day | 4.25 | 368 | 1564
| TOTAL |  |  |  | 1656
| Add 1% for water charges |  |  |  | 16.56
| TOTAL |  |  |  | 1672.56
| OVERHEADS & PROFIT @ 15 % |  |  |  | 250.88
| Cost for 10 cum |  |  |  | 1923.44
| Rate per Cum |  |  |  | 192.344
| Say |  |  |  | 192
192
Analysis of rate
14.2 | Excavation for cable trenches of depth upto 1.2 m in soft soil including getting out the excavated soil and disposal of surplus excavated soil as directed within a lead of 50 metres.
|  |  |  | DSR Rate Rs. | 194
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1016 | Mate | day | 0.25 | 368 | 92
1012 | Beldar/ coolie | day | 4.3 | 368 | 1582.4
| TOTAL |  |  |  | 1674.4
| Add 1% for water charges |  |  |  | 16.744
| TOTAL |  |  |  | 1691.144
| OVERHEADS & PROFIT @ 15 % |  |  |  | 253.67
| Cost for 10 cum |  |  |  | 1944.814
| Rate per Cum |  |  |  | 194.4814
| Say |  |  |  | 194
194
Analysis of rate
14.3 | Filling available excavated earth (excluding rock) in trenches, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 metres.
|  |  |  | DSR Rate Rs. | 124
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1016 | Mate | day | 0.2 | 368 | 73.6
1012 | Beldar/ coolie | day | 2.5 | 368 | 920
1013 | Bhisti | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 1067.2
| Add 1% for water charges |  |  |  | 10.672
| TOTAL |  |  |  | 1077.872
| OVERHEADS & PROFIT @ 15 % |  |  |  | 161.68
| Cost for 10 cum |  |  |  | 1239.552
| Rate per Cum |  |  |  | 123.9552
| Say |  |  |  | 124
124
Analysis of rate
14.4 | Excavation for cable trenches in soft soil, depth upto 1.2 m including dressing of sides lift upto 1.5 m, including getting out the excavated soil, refilling with sand and or good soil after laying of cable/ pipe etc in layers of 20 cm, ramming, watering and disposal of surplus excavated soil as directed, within a lead of 50 metres.
|  |  |  | DSR Rate Rs. | 318
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1016 | Mate | day | 0.25 | 368 | 92
1012 | Beldar/ coolie | day | 4.3 | 368 | 1582.4
1016 | Mate | day | 0.2 | 368 | 73.6
1012 | Beldar/ coolie | day | 2.5 | 368 | 920
1013 | Bhisti | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 2741.6
| Add 1% for water charges |  |  |  | 27.416
| TOTAL |  |  |  | 2769.016
| OVERHEADS & PROFIT @ 15 % |  |  |  | 415.35
| Cost for 10 cum |  |  |  | 3184.366
| Rate per Cum |  |  |  | 318.4366
| Say |  |  |  | 318
318
Analysis of rate
14.5 | Deduct for not consolidation by ramming and watering while re-filling with sand and or good soil in cable/ pipe laying.
|  |  |  | DSR Rate Rs. | 71
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1016 | Mate | day | 0.2 | 368 | 73.6
1012 | Beldar/ coolie | day | 1.25 | 368 | 460
1013 | Bhisti | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 607.2
| Add 1% for water charges |  |  |  | 6.072
| TOTAL |  |  |  | 613.272
| OVERHEADS & PROFIT @ 15 % |  |  |  | 91.99
| Cost for 10 cum |  |  |  | 705.262
| Rate per Cum |  |  |  | 70.5262
| Say |  |  |  | 71
71
Analysis of rate
14.6 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres.
|  |  |  | DSR Rate Rs. | 591
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
LABOUR
1015 | Stone Breaker | day | 5 | 407 | 2035
1014 | Excavator | day | 3 | 368 | 1104
1009 | Blacksmith, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 3 | 368 | 1104
1011 | Stone Chiseler | day | 2 | 407 | 814
| TOTAL |  |  |  | 5138.4
| OVERHEADS & PROFIT @ 15 % |  |  |  | 770.76
| Cost for 10 cum |  |  |  | 5909.16
| Rate per Cum |  |  |  | 590.916
| Say |  |  |  | 591
591
Analysis of rate
14.7 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required.
|  |  |  | DSR Rate Rs. | 5207
Details of cost for 1 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2950 | Stone aggregate (single size) 20mm nominal size | cum | 0.67 | 1175 | 787.25
2951 | Stone aggregate (single size) 10mm nominal size | cum | 0.22 | 1175 | 258.5
2952 | Coarse sand (Zone III) | cum | 0.45 | 1200 | 540
2948 | Cement | tonne | 0.32 | 5250 | 1680
| Total cost of materials |  |  |  | 3265.75
| Cartage @ 1 % of A1 |  |  |  | 32.6575
LABOUR
1010 | Mason, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 1.8 | 368 | 662.4
1013 | Bhisti | day | 1 | 368 | 368
9999 | Sundries | L.S. | 70 | 1.1 | 77
| TOTAL |  |  |  | 4487.2075
| Add 1% for water charges |  |  |  | 44.5455
| TOTAL |  |  |  | 4531.753
| OVERHEADS & PROFIT @ 15 % |  |  |  | 674.86
| TOTAL |  |  |  | 5206.613
| Rate per Cum |  |  |  | 5206.613
| Say |  |  |  | 5207
5207
Analysis of rate
14.8 | Providing and laying in position cement concrete 1:3:6 (1 cement : 2 coarse sand : 6 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required.
|  |  |  | DSR Rate Rs. | 4689
Details of cost for 1 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2950 | Stone aggregate (single size) 20mm nominal size | cum | 0.7 | 1175 | 822.5
2951 | Stone aggregate (single size) 10mm nominal size | cum | 0.24 | 1175 | 282
2952 | Coarse sand (Zone III) | cum | 0.47 | 1200 | 564
2948 | Cement | tonne | 0.22 | 5250 | 1155
| Total cost of materials |  |  |  | 2823.5
| Cartage @ 1 % of A1 |  |  |  | 28.235
LABOUR
1010 | Mason, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 1.8 | 368 | 662.4
1013 | Bhisti | day | 1 | 368 | 368
9999 | Sundries | L.S. | 70 | 1.1 | 77
| TOTAL |  |  |  | 4040.535
| Add 1% for water charges |  |  |  | 40.123
| TOTAL |  |  |  | 4080.658
| OVERHEADS & PROFIT @ 15 % |  |  |  | 607.86
| TOTAL |  |  |  | 4688.518
| Rate per Cum |  |  |  | 4688.518
| Say |  |  |  | 4689
4689
Analysis of rate
14.9 | Providing and laying in position cement concrete 1:3:6 (1 cement : 2 coarse sand : 6 graded stone aggregate 40 mm nominal size) in foundation of pump, DG set etc including form work etc as required.
|  |  |  | DSR Rate Rs. | 4525
Details of cost for 1 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2949 | Stone aggregate (single size) 40mm nominal size | cum | 0.65 | 1050 | 682.5
2950 | Stone aggregate (single size) 20mm nominal size | cum | 0.24 | 1175 | 282
2952 | Coarse sand (Zone III) | cum | 0.47 | 1200 | 564
2948 | Cement | tonne | 0.22 | 5250 | 1155
| Total cost of materials |  |  |  | 2683.5
| Cartage @ 1 % of A1 |  |  |  | 26.835
LABOUR
1010 | Mason, Grade 2 | day | 0.2 | 407 | 81.4
1012 | Beldar/ coolie | day | 1.8 | 368 | 662.4
1013 | Bhisti | day | 1 | 368 | 368
9999 | Sundries | L.S. | 70 | 1.1 | 77
| TOTAL |  |  |  | 3899.135
| Add 1% for water charges |  |  |  | 38.723
| TOTAL |  |  |  | 3937.858
| OVERHEADS & PROFIT @ 15 % |  |  |  | 586.65
| TOTAL |  |  |  | 4524.508
| Rate per Cum |  |  |  | 4524.508
| Say |  |  |  | 4525
4525
Analysis of rate
14.10 | Providing and laying in position reinforced cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required (excluding reinforcement).
|  |  |  | DSR Rate Rs. | 5487
Details of cost for 1 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2950 | Stone aggregate (single size) 20mm nominal size | cum | 0.67 | 1175 | 787.25
2951 | Stone aggregate (single size) 10mm nominal size | cum | 0.22 | 1175 | 258.5
2952 | Coarse sand (Zone III) | cum | 0.45 | 1200 | 540
2948 | Cement | tonne | 0.32 | 5250 | 1680
| Total cost of materials |  |  |  | 3265.75
| Cartage @ 1 % of A1 |  |  |  | 32.6575
LABOUR
1010 | Mason, Grade 2 | day | 0.25 | 407 | 101.75
1012 | Beldar/ coolie | day | 2.4 | 368 | 883.2
1013 | Bhisti | day | 1 | 368 | 368
9999 | Sundries | L.S. | 70 | 1.1 | 77
| TOTAL |  |  |  | 4728.3575
| Add 1% for water charges |  |  |  | 46.957
| TOTAL |  |  |  | 4775.3145
| OVERHEADS & PROFIT @ 15 % |  |  |  | 711.4
| TOTAL |  |  |  | 5486.7145
| Rate per Cum |  |  |  | 5486.7145
| Say |  |  |  | 5487
5487
Analysis of rate
14.11 | Providing brick work (in width 225 mm or more) with F.P.S. bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) at all levels.
|  |  |  | DSR Rate Rs. | 4105
Details of cost for 1 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2945 | Common burnt clay F.P.S. (non modular) bricks class designation 7.5 | each | 494 | 3 | 1482
2952 | Coarse sand (Zone III) | cum | 0.27 | 1200 | 324
2948 | Cement | tonne | 0.1 | 5250 | 525
| Total cost of materials |  |  |  | 2331
| Cartage @ 1 % of A1 |  |  |  | 23.31
LABOUR
1010 | Mason, Grade 2 | day | 0.9 | 407 | 366.3
1012 | Beldar/ coolie | day | 2 | 368 | 736
1013 | Bhisti | day | 0.22 | 368 | 80.96
| TOTAL |  |  |  | 3537.57
| Add 1% for water charges |  |  |  | 35.1426
| TOTAL |  |  |  | 3572.7126
| OVERHEADS & PROFIT @ 15 % |  |  |  | 532.41
| TOTAL |  |  |  | 4105.1226
| Rate per Cum |  |  |  | 4105.1226
| Say |  |  |  | 4105
4105
Analysis of rate
14.12 | Providing 15mm thick cement plaster of mix 1:4 (1 cement : 4 fine sand) at all levels.
|  |  |  | DSR Rate Rs. | 190
Details of cost for 10 sqm
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2946 | Fine sand | cum | 0.18 | 672 | 120.96
2948 | Cement | tonne | 0.07 | 5250 | 367.5
| Total cost of materials |  |  |  | 488.46
| Cartage @ 1 % of A1 |  |  |  | 4.8846
LABOUR
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1012 | Beldar/ coolie | day | 1 | 368 | 368
1013 | Bhisti | day | 1 | 368 | 368
| TOTAL |  |  |  | 1636.3446
| Add 1% for water charges |  |  |  | 16.3146
| TOTAL |  |  |  | 1652.6592
| OVERHEADS & PROFIT @ 15 % |  |  |  | 247.17
| Cost for 10 sqm |  |  |  | 1899.8292
| Rate per Sqm |  |  |  | 189.9829
| Say |  |  |  | 190
190
Analysis of rate
14.13 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required
14.13.1 | 50 mm dia |  |  | DSR Rate Rs. | 388
Details of cost for 30 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2832 | 50 mm dia. G.I. pipe (medium class) | metre | 30 | 276.86 | 8305.8
| Total cost of materials |  |  |  | 8305.8
| Cartage @ 1 % of A1 |  |  |  | 83.058
LABOUR
1004 | Fitter, Grade 1 | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
1012 | Beldar/ coolie | day | 4 | 368 | 1472
| TOTAL |  |  |  | 10129.808
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1519.47
| Cost for 30 Meters |  |  |  | 11649.278
| Rate per Meters |  |  |  | 388.3093
| Say |  |  |  | 388
388
Analysis of rate
14.13 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required
14.13.2 | 80 mm dia |  |  | DSR Rate Rs. | 592
Details of cost for 30 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2833 | 80 mm dia. G.I. pipe (medium class) | metre | 30 | 452.38 | 13571.4
| Total cost of materials |  |  |  | 13571.4
| Cartage @ 1 % of A1 |  |  |  | 135.714
LABOUR
1004 | Fitter, Grade 1 | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
1012 | Beldar/ coolie | day | 4 | 368 | 1472
| TOTAL |  |  |  | 15448.064
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2317.21
| Cost for 30 Meters |  |  |  | 17765.274
| Rate per Meters |  |  |  | 592.1758
| Say |  |  |  | 592
592
Analysis of rate
14.13 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required
14.13.3 | 100 mm dia |  |  | DSR Rate Rs. | 828
Details of cost for 30 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2834 | 100 mm dia. G.I. pipe (medium class) | metre | 30 | 655.39 | 19661.7
| Total cost of materials |  |  |  | 19661.7
| Cartage @ 1 % of A1 |  |  |  | 196.617
LABOUR
1004 | Fitter, Grade 1 | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
1012 | Beldar/ coolie | day | 4 | 368 | 1472
| TOTAL |  |  |  | 21599.267
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3239.89
| Cost for 30 Meters |  |  |  | 24839.157
| Rate per Meters |  |  |  | 827.9719
| Say |  |  |  | 828
828
Analysis of rate
14.13 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required
14.13.4 | 150 mm dia |  |  | DSR Rate Rs. | 1265
Details of cost for 30 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2835 | 150 mm dia. G.I. pipe (medium class) | metre | 30 | 1031.89 | 30956.7
| Total cost of materials |  |  |  | 30956.7
| Cartage @ 1 % of A1 |  |  |  | 309.567
LABOUR
1004 | Fitter, Grade 1 | day | 0.33 | 447 | 147.51
1007 | Khallasi | day | 0.33 | 368 | 121.44
1012 | Beldar/ coolie | day | 4 | 368 | 1472
| TOTAL |  |  |  | 33007.217
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4951.08
| Cost for 30 Meters |  |  |  | 37958.297
| Rate per Meters |  |  |  | 1265.2766
| Say |  |  |  | 1265
1265
Analysis of rate
14.14 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required.
14.14.1 | 100 mm dia |  |  | DSR Rate Rs. | 355
Details of cost for 10 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2841 | 100 mm dia RCC pipe NP2 class | metre | 10 | 141.75 | 1417.5
2845 | 100 mm dia RCC collar NP2 class | each | 5 | 21 | 105
2948 | Cement | tonne | 0.01 | 5250 | 52.5
2946 | Fine sand | cum | 0.01 | 672 | 6.72
| Total cost of materials |  |  |  | 1581.72
| Cartage @ 1 % of A1 |  |  |  | 15.8172
LABOUR
1010 | Mason, Grade 2 | day | 0.66 | 407 | 268.62
1012 | Beldar/ coolie | day | 0.66 | 368 | 242.88
1013 | Bhisti | day | 0.16 | 368 | 58.88
1012 | Beldar/ coolie | day | 2.5 | 368 | 920
| TOTAL |  |  |  | 3087.9172
| OVERHEADS & PROFIT @ 15 % |  |  |  | 463.19
| Cost for 10 Meters |  |  |  | 3551.1072
| Rate per Meters |  |  |  | 355.1107
| Say |  |  |  | 355
355
Analysis of rate
14.14 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required.
14.14.2 | 150 mm dia |  |  | DSR Rate Rs. | 405
Details of cost for 10 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2842 | 150 mm dia RCC pipe NP2 class | metre | 10 | 162 | 1620
2846 | 150 mm dia RCC collar NP2 class | each | 5 | 26 | 130
2948 | Cement | tonne | 0.01 | 5250 | 52.5
2946 | Fine sand | cum | 0.01 | 672 | 6.72
| Total cost of materials |  |  |  | 1809.22
| Cartage @ 1 % of A1 |  |  |  | 18.0922
LABOUR
1010 | Mason, Grade 2 | day | 0.8 | 407 | 325.6
1012 | Beldar/ coolie | day | 0.8 | 368 | 294.4
1013 | Bhisti | day | 0.16 | 368 | 58.88
1012 | Beldar/ coolie | day | 2.75 | 368 | 1012
| TOTAL |  |  |  | 3518.1922
| OVERHEADS & PROFIT @ 15 % |  |  |  | 527.73
| Cost for 10 Meters |  |  |  | 4045.9222
| Rate per Meters |  |  |  | 404.5922
| Say |  |  |  | 405
405
Analysis of rate
14.14 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required.
14.14.3 | 250 mm dia |  |  | DSR Rate Rs. | 478
Details of cost for 10 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2843 | 250 mm dia RCC pipe NP2 class | metre | 10 | 197 | 1970
2847 | 250 mm dia RCC collar NP2 class | each | 5 | 42 | 210
2948 | Cement | tonne | 0.01 | 5250 | 52.5
2946 | Fine sand | cum | 0.01 | 672 | 6.72
| Total cost of materials |  |  |  | 2239.22
| Cartage @ 1 % of A1 |  |  |  | 22.3922
LABOUR
1010 | Mason, Grade 2 | day | 1 | 407 | 407
1012 | Beldar/ coolie | day | 1 | 368 | 368
1013 | Bhisti | day | 0.2 | 368 | 73.6
1012 | Beldar/ coolie | day | 2.85 | 368 | 1048.8
| TOTAL |  |  |  | 4159.0122
| OVERHEADS & PROFIT @ 15 % |  |  |  | 623.85
| Cost for 10 Meters |  |  |  | 4782.8622
| Rate per Meters |  |  |  | 478.2862
| Say |  |  |  | 478
478
Analysis of rate
14.14 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required.
14.14.4 | 300 mm dia |  |  | DSR Rate Rs. | 592
Details of cost for 10 Meters
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
2844 | 300 mm dia RCC pipe NP2 class | metre | 10 | 274 | 2740
2848 | 300 mm dia RCC collar NP2 class | each | 4 | 51 | 204
2948 | Cement | tonne | 0.01 | 5250 | 52.5
2946 | Fine sand | cum | 0.02 | 672 | 13.44
| Total cost of materials |  |  |  | 3009.94
| Cartage @ 1 % of A1 |  |  |  | 30.0994
LABOUR
1010 | Mason, Grade 2 | day | 1.2 | 407 | 488.4
1012 | Beldar/ coolie | day | 1.2 | 368 | 441.6
1013 | Bhisti | day | 0.2 | 368 | 73.6
1012 | Beldar/ coolie | day | 3 | 368 | 1104
| TOTAL |  |  |  | 5147.6394
| OVERHEADS & PROFIT @ 15 % |  |  |  | 772.15
| Cost for 10 Meters |  |  |  | 5919.7894
| Rate per Meters |  |  |  | 591.9789
| Say |  |  |  | 592
592
CHAPTER 15 - LIGHTING CONTROLS (Analysis of rate based on DAR)
Analysis of rate
15.1 | Supplying, installation, testing and commissioning of Passive Infrared (PIR) technology based occupancy sensor having high performance, non regulating programmable type, suitable for connected load upto 10Amp, for mounting height up to 2.8 mtr and for 5 m diameter coverage area along with necessary fixing arrangements i/c programming at site etc. complete as required.
|  |  | DSR | Rate Rs. | 3193
Details of cost for 1 No
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1445 | PIR Occupancy sensor | each | 1 | 2587.5 | 2587.5
| Total cost of materials |  |  |  | 2587.5
| Cartage @ 1 % of A1 |  |  |  | 25.875
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 2776.375
| OVERHEADS & PROFIT @ 15 % |  |  |  | 416.46
| TOTAL |  |  |  | 3192.835
| Rate for 1 no. |  |  |  | 3192.835
| Say |  |  |  | 3193
3193
Analysis of rate
15.2 | Supplying, installation, testing and commissioning of Passive Infrared (PIR) technology based occupancy sensor with day light dimming (lighting level shall be regulated as per availability of natural day light in an area along with occupancy detection.) having high performance, regulating programmable type, suitable for connected load upto 10Amp, for mounting height up to 2.8 mtr and for 5 m diameter coverage area along with necessary fixing arrangements i/c programming at site etc. complete as required.
|  |  | DSR | Rate Rs. | 4467
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1446 | PIR Occupancy sensor With Day light dimming | each | 1 | 3684.37 | 3684.37
| Total cost of materials |  |  |  | 3684.37
| Cartage @ 1 % of A1 |  |  |  | 36.8437
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 3884.2137
| OVERHEADS & PROFIT @ 15 % |  |  |  | 582.63
| TOTAL |  |  |  | 4466.8437
| Rate for 1 no. |  |  |  | 4466.8437
| Say |  |  |  | 4467
4467
Analysis of rate
15.3 | Supplying, installation, testing and commissioning of Microwave technology based occupancy sensor having high performance, non regulating programmable type, suitable for connected load upto 10Amp, for mounting height up to 2.6 mtr and for 5m X 20m coverage area along with necessary fixing arrangements i/c programming at site etc. complete as required.
|  |  | DSR | Rate Rs. | 6100
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1447 | Microwave occupancy Sensor | each | 1 | 5090.62 | 5090.62
| Total cost of materials |  |  |  | 5090.62
| Cartage @ 1 % of A1 |  |  |  | 50.9062
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 5304.5262
| OVERHEADS & PROFIT @ 15 % |  |  |  | 795.68
| TOTAL |  |  |  | 6100.2062
| Rate for 1 no. |  |  |  | 6100.2062
| Say |  |  |  | 6100
6100
Analysis of rate
15.4 | Supplying, installation, testing and commissioning of Astronomical time switch of following configuration to be mounted in feeder pillars / Lighting DBs for automatic switching On & OFF of street lights at sun set & sun rise or twilight (Auto ON, Auto OFF, Auto modes) with manual override facility with 12/24 hour display format with suitable battery and indication for relay status i/c programming at site complete as required.
15.4.1 | 1 output per phase and suitable for single phase supply |  | DSR | Rate Rs. | 2566
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1448 | Astrononical time switch suitable for 1 output per phase and suitable for single phase supply | each | 1 | 2047.5 | 2047.5
| Total cost of materials |  |  |  | 2047.5
| Cartage @ 1 % of A1 |  |  |  | 20.475
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 2230.975
| OVERHEADS & PROFIT @ 15 % |  |  |  | 334.65
| TOTAL |  |  |  | 2565.625
| Rate for 1 no. |  |  |  | 2565.625
| Say |  |  |  | 2566
2566
Analysis of rate
15.4 | Supplying, installation, testing and commissioning of Astronomical time switch of following configuration to be mounted in feeder pillars / Lighting DBs for automatic switching On & OFF of street lights at sun set & sun rise or twilight (Auto ON, Auto OFF, Auto modes) with manual override facility with 12/24 hour display format with suitable battery and indication for relay status i/c programming at site complete as required.
15.4.2 | 2 output per phase and suitable for single phase supply |  | DSR | Rate Rs. | 5329
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1449 | Astrononical time switch suitable for2 output per phase and suitable for single phase supply | each | 1 | 4426.5 | 4426.5
| Total cost of materials |  |  |  | 4426.5
| Cartage @ 1 % of A1 |  |  |  | 44.265
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 4633.765
| OVERHEADS & PROFIT @ 15 % |  |  |  | 695.06
| TOTAL |  |  |  | 5328.825
| Rate for 1 no. |  |  |  | 5328.825
| Say |  |  |  | 5329
5329
Analysis of rate
15.4 | Supplying, installation, testing and commissioning of Astronomical time switch of following configuration to be mounted in feeder pillars / Lighting DBs for automatic switching On & OFF of street lights at sun set & sun rise or twilight (Auto ON, Auto OFF, Auto modes) with manual override facility with 12/24 hour display format with suitable battery and indication for relay status i/c programming at site complete as required.
15.4.3 | 3 output (1output per phase) and suitable for three phase supply |  | DSR | Rate Rs. | 6254
Details of cost for 10 cum
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
MATERIALS
1450 | Astrononical time switch suitable for 3output(1output per phase) and suitable for three phase supply | each | 1 | 5222.75 | 5222.75
| Total cost of materials |  |  |  | 5222.75
| Cartage @ 1 % of A1 |  |  |  | 52.2275
LABOUR
1001 | Wireman | day | 0.2 | 447 | 89.4
1007 | Khallasi | day | 0.2 | 368 | 73.6
| TOTAL |  |  |  | 5437.9775
| OVERHEADS & PROFIT @ 15 % |  |  |  | 815.7
| TOTAL |  |  |  | 6253.6775
| Rate for 1 no. |  |  |  | 6253.6775
| Say |  |  |  | 6254
6254
CHAPTER 16 - HVAC (Analysis of rate based on DAR)
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.1 | Chilled water piping of nominal size - 400 mm dia. (65mm thick fiber glass insulation) |  | DSR | Rate Rs. | 10309
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3001 | M.S. Pipe - 400 mm dia. (Heavy Class, 7 mm thick MS Sheet) | Mtr | 10 | 5040.63 | 50406.3
| add for wastage @ 5% |  |  |  | 2520.315
| Total of (A1) |  |  |  | 52926.615
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 7938.9923
| Total of (A1 + A2) |  |  |  | 60865.6073
A(3) Basic Price of
4001 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-65 mm thickness for 400 mm dia pipe | Mtr | 10 | 1507.13 | 15071.3
| add for wastage @ 10% |  |  |  | 1507.13
| Total of (A3) |  |  |  | 16578.43
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 16.65 | 300 | 4995
| add for wastage @ 10% |  |  |  | 499.5
| Total of (A4) |  |  |  | 5494.5
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 82938.5373
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 829.3854
| Total of A |  |  |  | 83767.9226
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 3 | 447 | 1341
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 4.75 | 368 | 1748
| Total of B(1) |  |  |  | 3841.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(3) |  |  |  | 1018.75
| Total of B |  |  |  | 5878.75
| Total of A+B |  |  |  | 89646.6726
| OVERHEADS & PROFIT @ 15 % |  |  |  | 13447
| Total |  |  |  | 103093.6726
| Rate per metre |  |  |  | 10309.3673
| Say |  |  |  | 10309
10309
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.2 | Chilled water piping of nominal size - 350 mm dia. (65mm thick fiber glass insulation) |  | DSR | Rate Rs. | 7120
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3002 | M.S. Pipe - 350 mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2955.02 | 29550.2
| add for wastage @ 5% |  |  |  | 1477.51
| Total of (A1) |  |  |  | 31027.71
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 4654.1565
| Total of (A1 + A2) |  |  |  | 35681.8665
A(3) Basic Price of
4002 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-65 mm thickness for 350 mm dia pipe | Mtr | 10 | 1347.1 | 13471
| add for wastage @ 10% |  |  |  | 1347.1
| Total of (A3) |  |  |  | 14818.1
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 15.08 | 300 | 4524
| add for wastage @ 10% |  |  |  | 452.4
| Total of (A4) |  |  |  | 4976.4
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 55476.3665
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 554.7637
| Total of A |  |  |  | 56031.1302
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 3 | 447 | 1341
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 4.75 | 368 | 1748
| Total of B(1) |  |  |  | 3841.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(3) |  |  |  | 1018.75
| Total of B |  |  |  | 5878.75
| Total of A+B |  |  |  | 61909.8802
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9286.48
| Total |  |  |  | 71196.3602
| Rate per metre |  |  |  | 7119.636
| Say |  |  |  | 7120
7120
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.3 | Chilled water piping of nominal size - 300 mm dia. (65mm thick fiber glass insulation) |  | DSR | Rate Rs. | 6354
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3003 | M.S. Pipe- 300 mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2673.41 | 26734.1
| add for wastage @ 5% |  |  |  | 1336.705
| Total of (A1) |  |  |  | 28070.805
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 4210.6208
| Total of (A1 + A2) |  |  |  | 32281.4258
A(3) Basic Price of
4003 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-65 mm thickness for 300 mm dia pipe | Mtr | 10 | 1104.16 | 11041.6
| add for wastage @ 10% |  |  |  | 1104.16
| Total of (A3) |  |  |  | 12145.76
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 13.51 | 300 | 4053
| add for wastage @ 10% |  |  |  | 405.3
| Total of (A4) |  |  |  | 4458.3
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 48885.4858
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 488.8549
| Total of A |  |  |  | 49374.3406
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 3 | 447 | 1341
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 4.75 | 368 | 1748
| Total of B(1) |  |  |  | 3841.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(3) |  |  |  | 1018.75
| Total of B |  |  |  | 5878.75
| Total of A+B |  |  |  | 55253.0906
| OVERHEADS & PROFIT @ 15 % |  |  |  | 8287.96
| Total |  |  |  | 63541.0506
| Rate per metre |  |  |  | 6354.1051
| Say |  |  |  | 6354
6354
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.4 | Chilled water piping of nominal size - 250 mm dia. (50mm thick fiber glass insulation) |  | DSR | Rate Rs. | 5369
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3004 | M.S. Pipe - 250mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2249.1 | 22491
| add for wastage @ 5% |  |  |  | 1124.55
| Total of (A1) |  |  |  | 23615.55
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 3542.3325
| Total of (A1 + A2) |  |  |  | 27157.8825
A(3) Basic Price of
4004 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-50 mm thickness for 250 mm dia pipe | Mtr | 10 | 964.69 | 9646.9
| add for wastage @ 10% |  |  |  | 964.69
| Total of (A3) |  |  |  | 10611.59
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 11 | 300 | 3300
| add for wastage @ 10% |  |  |  | 330
| Total of (A4) |  |  |  | 3630
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 41399.4725
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 413.9947
| Total of A |  |  |  | 41813.4672
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 4 | 368 | 1472
| Total of B(1) |  |  |  | 3240
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(2) |  |  |  | 815
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(3) |  |  |  | 815
| Total of B |  |  |  | 4870
| Total of A+B |  |  |  | 46683.4672
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7002.52
| Total |  |  |  | 53685.9872
| Rate per metre |  |  |  | 5368.5987
| Say |  |  |  | 5369
5369
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.5 | Chilled water piping of nominal size - 200 mm dia. (50mm thick fiber glass insulation) |  | DSR | Rate Rs. | 4479
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3005 | M.S. Pipe - 200mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 1792.67 | 17926.7
| add for wastage @ 5% |  |  |  | 896.335
| Total of (A1) |  |  |  | 18823.035
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 2823.4552
| Total of (A1 + A2) |  |  |  | 21646.4902
A(3) Basic Price of
4005 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-50 mm thickness for 200 mm dia pipe | Mtr | 10 | 816.87 | 8168.7
| add for wastage @ 10% |  |  |  | 816.87
| Total of (A3) |  |  |  | 8985.57
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 9.426 | 300 | 2827.8
| add for wastage @ 10% |  |  |  | 282.78
| Total of (A4) |  |  |  | 3110.58
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 33742.6402
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 337.4264
| Total of A |  |  |  | 34080.0667
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 4 | 368 | 1472
| Total of B(1) |  |  |  | 3240
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(2) |  |  |  | 815
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(3) |  |  |  | 815
| Total of B |  |  |  | 4870
| Total of A+B |  |  |  | 38950.0667
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5842.51
| Total |  |  |  | 44792.5767
| Rate per metre |  |  |  | 4479.2577
| Say |  |  |  | 4479
4479
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.6 | Chilled water piping of nominal size - 150 mm dia. (50mm thick fiber glass insulation) |  | DSR | Rate Rs. | 2939
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3006 | M.S. Pipe - 150mm dia. (C-Class) | Mtr | 10 | 1138.54 | 11385.4
| add for wastage @ 5% |  |  |  | 569.27
| Total of (A1) |  |  |  | 11954.67
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 1793.2005
| Total of (A1 + A2) |  |  |  | 13747.8705
A(3) Basic Price of
4006 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-50 mm thickness for 150 mm dia pipe | Mtr | 10 | 413.26 | 4132.6
| add for wastage @ 10% |  |  |  | 413.26
| Total of (A3) |  |  |  | 4545.86
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 7.855 | 300 | 2356.5
| add for wastage @ 10% |  |  |  | 235.65
| Total of (A4) |  |  |  | 2592.15
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 20885.8805
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 208.8588
| Total of A |  |  |  | 21094.7393
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 3.5 | 368 | 1288
| Total of B(1) |  |  |  | 2832.5
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(2) |  |  |  | 815
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(3) |  |  |  | 815
| Total of B |  |  |  | 4462.5
| Total of A+B |  |  |  | 25557.2393
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3833.59
| Total |  |  |  | 29390.8293
| Rate per metre |  |  |  | 2939.0829
| Say |  |  |  | 2939
2939
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.7 | Chilled water piping of nominal size - 125 mm dia. (40mm thick fiber glass insulation) |  | DSR | Rate Rs. | 2499
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3007 | M.S. Pipe - 125mm dia. (C-Class) | Mtr | 10 | 958.28 | 9582.8
| add for wastage @ 5% |  |  |  | 479.14
| Total of (A1) |  |  |  | 10061.94
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 1509.291
| Total of (A1 + A2) |  |  |  | 11571.231
A(3) Basic Price of
4007 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-40 mm thickness for 125 mm dia pipe | Mtr | 10 | 364.41 | 3644.1
| add for wastage @ 10% |  |  |  | 364.41
| Total of (A3) |  |  |  | 4008.51
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 6.441 | 300 | 1932.3
| add for wastage @ 10% |  |  |  | 193.23
| Total of (A4) |  |  |  | 2125.53
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 17705.271
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 177.0527
| Total of A |  |  |  | 17882.3237
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 0.75 | 447 | 335.25
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 3.25 | 368 | 1196
| Total of B(1) |  |  |  | 2628.75
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(2) |  |  |  | 611.25
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(3) |  |  |  | 611.25
| Total of B |  |  |  | 3851.25
| Total of A+B |  |  |  | 21733.5737
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3260.04
| Total |  |  |  | 24993.6137
| Rate per metre |  |  |  | 2499.3614
| Say |  |  |  | 2499
2499
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.8 | Chilled water piping of nominal size - 100 mm dia. (40mm thick fiber glass insulation) |  | DSR | Rate Rs. | 2167
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3008 | M.S. Pipe - 100mm dia. (C-Class) | Mtr | 10 | 776.98 | 7769.8
| add for wastage @ 5% |  |  |  | 388.49
| Total of (A1) |  |  |  | 8158.29
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 1223.7435
| Total of (A1 + A2) |  |  |  | 9382.0335
A(3) Basic Price of
4008 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-40 mm thickness for 100 mm dia pipe | Mtr | 10 | 315.57 | 3155.7
| add for wastage @ 10% |  |  |  | 315.57
| Total of (A3) |  |  |  | 3471.27
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 5.656 | 300 | 1696.8
| add for wastage @ 10% |  |  |  | 169.68
| Total of (A4) |  |  |  | 1866.48
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 14719.7835
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 147.1978
| Total of A |  |  |  | 14866.9813
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 0.75 | 447 | 335.25
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 3.25 | 368 | 1196
| Total of B(1) |  |  |  | 2750.5
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(2) |  |  |  | 611.25
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(3) |  |  |  | 611.25
| Total of B |  |  |  | 3973
| Total of A+B |  |  |  | 18839.9813
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2826
| Total |  |  |  | 21665.9813
| Rate per metre |  |  |  | 2166.5981
| Say |  |  |  | 2167
2167
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.9 | Chilled water piping of nominal size - 80 mm dia. (25mm thick fiber glass insulation) |  | DSR | Rate Rs. | 1638
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3009 | M.S. Pipe - 80mm dia. (C-Class) | Mtr | 10 | 527.4 | 5274
| add for wastage @ 5% |  |  |  | 263.7
| Total of (A1) |  |  |  | 5537.7
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 830.655
| Total of (A1 + A2) |  |  |  | 6368.355
A(3) Basic Price of
4009 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-25 mm thickness for 80 mm dia pipe | Mtr | 10 | 269.29 | 2692.9
| add for wastage @ 10% |  |  |  | 269.29
| Total of (A3) |  |  |  | 2962.19
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 4.085 | 300 | 1225.5
| add for wastage @ 10% |  |  |  | 122.55
| Total of (A4) |  |  |  | 1348.05
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 10678.595
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 106.7859
| Total of A |  |  |  | 10785.3809
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.75 | 368 | 1012
| Total of B(1) |  |  |  | 2231.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(2) |  |  |  | 611.25
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(3) |  |  |  | 611.25
| Total of B |  |  |  | 3453.75
| Total of A+B |  |  |  | 14239.1309
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2135.87
| Total |  |  |  | 16375.0009
| Rate per metre |  |  |  | 1637.5001
| Say |  |  |  | 1638
1638
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.10 | Chilled water piping of nominal size - 65 mm dia. (25mm thick fiber glass insulation) |  | DSR | Rate Rs. | 1412
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3010 | M.S. Pipe -65mm dia. (C-Class) | Mtr | 10 | 435.46 | 4354.6
| add for wastage @ 5% |  |  |  | 217.73
| Total of (A1) |  |  |  | 4572.33
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 685.8495
| Total of (A1 + A2) |  |  |  | 5258.1795
A(3) Basic Price of
4010 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-25 mm thickness for 65 mm dia pipe | Mtr | 10 | 244.23 | 2442.3
| add for wastage @ 10% |  |  |  | 244.23
| Total of (A3) |  |  |  | 2686.53
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 3.613 | 300 | 1083.9
| add for wastage @ 10% |  |  |  | 108.39
| Total of (A4) |  |  |  | 1192.29
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 9136.9995
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 91.37
| Total of A |  |  |  | 9228.3695
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.75 | 368 | 1012
| Total of B(1) |  |  |  | 2231.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(3) |  |  |  | 407.5
| Total of B |  |  |  | 3046.25
| Total of A+B |  |  |  | 12274.6195
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1841.19
| Total |  |  |  | 14115.8095
| Rate per metre |  |  |  | 1411.5809
| Say |  |  |  | 1412
1412
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.11 | Chilled water piping of nominal size - 50 mm dia. (25mm thick fiber glass insulation) |  | DSR | Rate Rs. | 1163
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3011 | M.S. Pipe -50 mm dia. (C-Class) | Mtr | 10 | 332.26 | 3322.6
| add for wastage @ 5% |  |  |  | 166.13
| Total of (A1) |  |  |  | 3488.73
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 523.3095
| Total of (A1 + A2) |  |  |  | 4012.0395
A(3) Basic Price of
4011 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-25 mm thickness for 50 mm dia pipe | Mtr | 10 | 213.38 | 2133.8
| add for wastage @ 10% |  |  |  | 213.38
| Total of (A3) |  |  |  | 2347.18
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 3.142 | 300 | 942.6
| add for wastage @ 10% |  |  |  | 94.26
| Total of (A4) |  |  |  | 1036.86
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 7396.0795
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 73.9608
| Total of A |  |  |  | 7470.0403
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.5 | 447 | 670.5
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.25 | 368 | 828
| Total of B(1) |  |  |  | 1823.75
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(3) |  |  |  | 407.5
| Total of B |  |  |  | 2638.75
| Total of A+B |  |  |  | 10108.7903
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1516.32
| Total |  |  |  | 11625.1103
| Rate per metre |  |  |  | 1162.511
| Say |  |  |  | 1163
1163
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.12 | Chilled water piping of nominal size - 40 mm dia. (25mm thick fiber glass insulation) |  | DSR | Rate Rs. | 986
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3012 | M.S. Pipe - 40 mm dia. (C-Class) | Mtr | 10 | 234.64 | 2346.4
| add for wastage @ 5% |  |  |  | 117.32
| Total of (A1) |  |  |  | 2463.72
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 369.558
| Total of (A1 + A2) |  |  |  | 2833.278
A(3) Basic Price of
4012 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-25 mm thickness for 40 mm dia pipe | Mtr | 10 | 192.17 | 1921.7
| add for wastage @ 10% |  |  |  | 192.17
| Total of (A3) |  |  |  | 2113.87
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 2.828 | 300 | 848.4
| add for wastage @ 10% |  |  |  | 84.84
| Total of (A4) |  |  |  | 933.24
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 5880.388
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 58.8039
| Total of A |  |  |  | 5939.1919
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.5 | 447 | 670.5
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.25 | 368 | 828
| Total of B(1) |  |  |  | 1823.75
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(3) |  |  |  | 407.5
| Total of B |  |  |  | 2638.75
| Total of A+B |  |  |  | 8577.9419
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1286.69
| Total |  |  |  | 9864.6319
| Rate per metre |  |  |  | 986.4632
| Say |  |  |  | 986
986
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.13 | Chilled water piping of nominal size - 32 mm dia. (25mm thick fiber glass insulation) |  | DSR | Rate Rs. | 869
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3013 | M.S. Pipe - 32 mm dia (C-Class) | Mtr | 10 | 201.71 | 2017.1
| add for wastage @ 5% |  |  |  | 100.855
| Total of (A1) |  |  |  | 2117.955
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 317.6932
| Total of (A1 + A2) |  |  |  | 2435.6482
A(3) Basic Price of
4013 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-25 mm thickness for 32 mm dia pipe | Mtr | 10 | 180.6 | 1806
| add for wastage @ 10% |  |  |  | 180.6
| Total of (A3) |  |  |  | 1986.6
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 2.576 | 300 | 772.8
| add for wastage @ 10% |  |  |  | 77.28
| Total of (A4) |  |  |  | 850.08
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 5272.3282
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 52.7233
| Total of A |  |  |  | 5325.0515
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1087 | Welder | day | 0.25 | 447 | 111.75
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 1.75 | 368 | 644
| Total of B(1) |  |  |  | 1416.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(3) |  |  |  | 407.5
| Total of B |  |  |  | 2231.25
| Total of A+B |  |  |  | 7556.3015
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1133.45
| Total |  |  |  | 8689.7515
| Rate per metre |  |  |  | 868.9752
| Say |  |  |  | 869
869
Analysis of rate
16.1 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with 80 kg/cum density resin bonded fiber glass pipe section insulation covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date ) at joints and repairing of damage to building etc. as per specifications and as required. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.1.14 | Chilled water piping of nominal size - 25 mm dia. (25mm thick fiber glass insulation) |  | DSR | Rate Rs. | 777
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3014 | M.S. Pipe - 25 mm dia (C-Class) | Mtr | 10 | 156.59 | 1565.9
| add for wastage @ 5% |  |  |  | 78.295
| Total of (A1) |  |  |  | 1644.195
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 246.6293
| Total of (A1 + A2) |  |  |  | 1890.8243
A(3) Basic Price of
4014 | Resin bonded fiber glass pipe section insulation having density 80 kg/cum-25 mm thickness for 25 mm dia pipe | Mtr | 10 | 164.53 | 1645.3
| add for wastage @ 10% |  |  |  | 164.53
| Total of (A3) |  |  |  | 1809.83
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 2.357 | 300 | 707.1
| add for wastage @ 10% |  |  |  | 70.71
| Total of (A4) |  |  |  | 777.81
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 4478.4642
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 44.7846
| Total of A |  |  |  | 4523.2489
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1087 | Welder | day | 0.25 | 447 | 111.75
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 1.75 | 368 | 644
| Total of B(1) |  |  |  | 1416.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(3) |  |  |  | 407.5
| Total of B |  |  |  | 2231.25
| Total of A+B |  |  |  | 6754.4989
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1013.17
| Total |  |  |  | 7767.6689
| Rate per metre |  |  |  | 776.7669
| Say |  |  |  | 777
777
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.1 | Chilled water piping of nominal size - 400 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 8662
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3001 | M.S. Pipe - 400 mm dia. (Heavy Class, 7 mm thick MS Sheet) | Mtr | 10 | 5040.63 | 50406.3
| add for wastage @ 5% |  |  |  | 2520.315
| Total of (A1) |  |  |  | 52926.615
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 7938.9923
| Total of (A1 + A2) |  |  |  | 60865.6073
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Mtr | 12.57 | 658.35 | 8275.46
| add for wastage @ 10% |  |  |  | 827.546
| Total of (A3) |  |  |  | 9103.006
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 0 | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 69968.6133
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 699.6861
| Total of A |  |  |  | 70668.2994
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 3 | 447 | 1341
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 4.75 | 368 | 1748
| Total of B(1) |  |  |  | 3841.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(2) |  |  |  | 815
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0 | 447 | 0
1007 | Helper/Khallasi | day | 0 | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 4656.25
| Total of A+B |  |  |  | 75324.5494
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11298.68
| Total |  |  |  | 86623.2294
| Rate per metre |  |  |  | 8662.3229
| Say |  |  |  | 8662
8662
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.2 | Chilled water piping of nominal size - 350 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 5605
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3002 | M.S. Pipe - 350 mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2955.02 | 29550.2
| add for wastage @ 5% |  |  |  | 1477.51
| Total of (A1) |  |  |  | 31027.71
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 4654.1565
| Total of (A1 + A2) |  |  |  | 35681.8665
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Mtr | 10.997 | 658.35 | 7239.87
| add for wastage @ 10% |  |  |  | 723.987
| Total of (A3) |  |  |  | 7963.857
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 43645.7235
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 436.4572
| Total of A |  |  |  | 44082.1807
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 3 | 447 | 1341
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 4.75 | 368 | 1748
| Total of B(1) |  |  |  | 3841.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(2) |  |  |  | 815
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 4656.25
| Total of A+B |  |  |  | 48738.4307
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7310.76
| Total |  |  |  | 56049.1907
| Rate per metre |  |  |  | 5604.9191
| Say |  |  |  | 5605
5605
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.3 | Chilled water piping of nominal size - 300 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 5074
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3003 | M.S. Pipe- 300 mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2673.41 | 26734.1
| add for wastage @ 5% |  |  |  | 1336.705
| Total of (A1) |  |  |  | 28070.805
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 4210.6208
| Total of (A1 + A2) |  |  |  | 32281.4258
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Mtr | 9.429 | 658.35 | 6207.58
| add for wastage @ 10% |  |  |  | 620.758
| Total of (A3) |  |  |  | 6828.338
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm | 0 | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 39109.7637
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 391.0976
| Total of A |  |  |  | 39500.8614
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 3 | 447 | 1341
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 4.75 | 368 | 1748
| Total of B(1) |  |  |  | 3841.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(2) |  |  |  | 815
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 4656.25
| Total of A+B |  |  |  | 44157.1114
| OVERHEADS & PROFIT @ 15 % |  |  |  | 6623.57
| Total |  |  |  | 50780.6814
| Rate per metre |  |  |  | 5078.0681
| Say |  |  |  | 5078
5078
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.4 | Chilled water piping of nominal size - 250 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 4390
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3004 | M.S. Pipe - 250mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2249.1 | 22491
| add for wastage @ 5% |  |  |  | 1124.55
| Total of (A1) |  |  |  | 23615.55
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 3542.3325
| Total of (A1 + A2) |  |  |  | 27157.8825
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Mtr | 9.426 | 658.35 | 6205.61
| add for wastage @ 10% |  |  |  | 620.561
| Total of (A3) |  |  |  | 6826.171
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 33984.0535
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 339.8405
| Total of A |  |  |  | 34323.894
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 4 | 368 | 1472
| Total of B(1) |  |  |  | 3240
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(2) |  |  |  | 611.25
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 3851.25
| Total of A+B |  |  |  | 38175.144
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5726.27
| Total |  |  |  | 43901.414
| Rate per metre |  |  |  | 4390.1414
| Say |  |  |  | 4390
4390
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.5 | Chilled water piping of nominal size - 200 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 3504
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3005 | M.S. Pipe - 200mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 1792.67 | 17926.7
| add for wastage @ 5% |  |  |  | 896.335
| Total of (A1) |  |  |  | 18823.035
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 2823.4552
| Total of (A1 + A2) |  |  |  | 21646.4902
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Mtr | 6.5 | 658.35 | 4279.28
| add for wastage @ 10% |  |  |  | 427.928
| Total of (A3) |  |  |  | 4707.208
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 26353.6982
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 263.537
| Total of A |  |  |  | 26617.2352
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 4 | 368 | 1472
| Total of B(1) |  |  |  | 3240
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(2) |  |  |  | 611.25
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 3851.25
| Total of A+B |  |  |  | 30468.4852
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4570.27
| Total |  |  |  | 35038.7552
| Rate per metre |  |  |  | 3503.8755
| Say |  |  |  | 3504
3504
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.6 | Chilled water piping of nominal size - 150 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 2439
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3006 | M.S. Pipe - 150mm dia. (C-Class) | Mtr | 10 | 1138.54 | 11385.4
| add for wastage @ 5% |  |  |  | 569.27
| Total of (A1) |  |  |  | 11954.67
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 1793.2005
| Total of (A1 + A2) |  |  |  | 13747.8705
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Mtr | 4.75 | 658.35 | 3127.16
| add for wastage @ 10% |  |  |  | 312.716
| Total of (A3) |  |  |  | 3439.876
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 17187.7465
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 171.8775
| Total of A |  |  |  | 17359.624
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 4 | 368 | 1472
| Total of B(1) |  |  |  | 3240
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(2) |  |  |  | 611.25
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 3851.25
| Total of A+B |  |  |  | 21210.874
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3181.63
| Total |  |  |  | 24392.504
| Rate per metre |  |  |  | 2439.2504
| Say |  |  |  | 2439
2439
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.7 | Chilled water piping of nominal size - 125 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 2142
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3007 | M.S. Pipe - 125mm dia. (C-Class) | Mtr | 10 | 958.28 | 9582.8
| add for wastage @ 5% |  |  |  | 479.14
| Total of (A1) |  |  |  | 10061.94
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 1509.291
| Total of (A1 + A2) |  |  |  | 11571.231
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Mtr | 4.5 | 658.35 | 2962.58
| add for wastage @ 10% |  |  |  | 296.258
| Total of (A3) |  |  |  | 3258.838
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 14830.069
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 148.3007
| Total of A |  |  |  | 14978.3697
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 0.75 | 447 | 335.25
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 3.75 | 368 | 1380
| Total of B(1) |  |  |  | 3036.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(2) |  |  |  | 611.25
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 3647.5
| Total of A+B |  |  |  | 18625.8697
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2793.88
| Total |  |  |  | 21419.7497
| Rate per metre |  |  |  | 2141.975
| Say |  |  |  | 2142
2142
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.8 | Chilled water piping of nominal size - 100 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 1709
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3008 | M.S. Pipe - 100mm dia. (C-Class) | Mtr | 10 | 776.98 | 7769.8
| add for wastage @ 5% |  |  |  | 388.49
| Total of (A1) |  |  |  | 8158.29
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 1223.7435
| Total of (A1 + A2) |  |  |  | 9382.0335
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Mtr | 3.5 | 658.35 | 2304.23
| add for wastage @ 10% |  |  |  | 230.423
| Total of (A3) |  |  |  | 2534.653
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 11916.6865
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 119.1669
| Total of A |  |  |  | 12035.8534
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 0.75 | 447 | 335.25
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 3 | 368 | 1104
| Total of B(1) |  |  |  | 2435
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 2842.5
| Total of A+B |  |  |  | 14878.3534
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2231.75
| Total |  |  |  | 17110.1034
| Rate per metre |  |  |  | 1711.0103
| Say |  |  |  | 1711
1711
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.9 | Chilled water piping of nominal size - 80 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 1255
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3009 | M.S. Pipe - 80mm dia. (C-Class) | Mtr | 10 | 527.4 | 5274
| add for wastage @ 5% |  |  |  | 263.7
| Total of (A1) |  |  |  | 5537.7
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 830.655
| Total of (A1 + A2) |  |  |  | 6368.355
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Mtr | 2.514 | 658.35 | 1655.09
| add for wastage @ 10% |  |  |  | 165.509
| Total of (A3) |  |  |  | 1820.599
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 8188.954
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 81.8895
| Total of A |  |  |  | 8270.8435
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.75 | 368 | 1012
| Total of B(1) |  |  |  | 2231.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 2638.75
| Total of A+B |  |  |  | 10909.5935
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1636.44
| Total |  |  |  | 12546.0335
| Rate per metre |  |  |  | 1254.6034
| Say |  |  |  | 1255
1255
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.10 | Chilled water piping of nominal size - 65 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 1030
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3010 | M.S. Pipe -65mm dia. (C-Class) | Mtr | 10 | 435.46 | 4354.6
| add for wastage @ 5% |  |  |  | 217.73
| Total of (A1) |  |  |  | 4572.33
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 685.8495
| Total of (A1 + A2) |  |  |  | 5258.1795
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Mtr | 2.042 | 658.35 | 1344.35
| add for wastage @ 10% |  |  |  | 134.435
| Total of (A3) |  |  |  | 1478.785
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Sqm |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 6736.9645
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 67.3696
| Total of A |  |  |  | 6804.3341
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.5 | 447 | 670.5
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.25 | 368 | 828
| Total of B(1) |  |  |  | 1823.75
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.4 | 447 | 178.8
1007 | Helper/Khallasi | day | 0.4 | 368 | 147.2
| Total of B(2) |  |  |  | 326
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 2149.75
| Total of A+B |  |  |  | 8954.0841
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1343.11
| Total |  |  |  | 10297.1941
| Rate per metre |  |  |  | 1029.7194
| Say |  |  |  | 1030
1030
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.11 | Chilled water piping of nominal size - 50 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 881
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3011 | M.S. Pipe -50 mm dia. (C-Class) | Mtr | 10 | 332.26 | 3322.6
| add for wastage @ 5% |  |  |  | 166.13
| Total of (A1) |  |  |  | 3488.73
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 523.3095
| Total of (A1 + A2) |  |  |  | 4012.0395
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Sqmtr | 2 | 658.35 | 1316.7
| add for wastage @ 10% |  |  |  | 131.67
| Total of (A3) |  |  |  | 1448.37
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 5460.4095
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 54.6041
| Total of A |  |  |  | 5515.0136
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.5 | 447 | 670.5
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.25 | 368 | 828
| Total of B(1) |  |  |  | 1823.75
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.4 | 447 | 178.8
1007 | Helper/Khallasi | day | 0.4 | 368 | 147.2
| Total of B(2) |  |  |  | 326
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 2149.75
| Total of A+B |  |  |  | 7664.7636
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1149.71
| Total |  |  |  | 8814.4736
| Rate per metre |  |  |  | 881.4474
| Say |  |  |  | 881
881
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.12 | Chilled water piping of nominal size - 40 mm dia. (32mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 702
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3012 | M.S. Pipe - 40 mm dia. (C-Class) | Mtr | 10 | 234.64 | 2346.4
| add for wastage @ 5% |  |  |  | 117.32
| Total of (A1) |  |  |  | 2463.72
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 369.558
| Total of (A1 + A2) |  |  |  | 2833.278
A(3) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Sqmtr | 1.5 | 658.35 | 987.53
| add for wastage @ 10% |  |  |  | 98.753
| Total of (A3) |  |  |  | 1086.283
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 3919.561
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 39.1956
| Total of A |  |  |  | 3958.7566
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.5 | 447 | 670.5
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.25 | 368 | 828
| Total of B(1) |  |  |  | 1823.75
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.4 | 447 | 178.8
1007 | Helper/Khallasi | day | 0.4 | 368 | 147.2
| Total of B(2) |  |  |  | 326
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 2149.75
| Total of A+B |  |  |  | 6108.5066
| OVERHEADS & PROFIT @ 15 % |  |  |  | 916.28
| Total |  |  |  | 7024.7866
| Rate per metre |  |  |  | 702.4787
| Say |  |  |  | 702
702
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.13 | Chilled water piping of nominal size - 32 mm dia. (19mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 564
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3013 | M.S. Pipe - 32 mm dia (C-Class) | Mtr | 10 | 201.71 | 2017.1
| add for wastage @ 5% |  |  |  | 100.855
| Total of (A1) |  |  |  | 2117.955
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 317.6932
| Total of (A1 + A2) |  |  |  | 2435.6482
A(3) Basic Price of
4016 | Nitrile rubber (cross link closed cell preformed sections of polyethylene) Insulation -19 mm thickness dia pipe | Sqmtr | 1.2 | 371.8 | 446.16
| add for wastage @ 10% |  |  |  | 44.616
| Total of (A3) |  |  |  | 490.776
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 2926.4242
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 29.2642
| Total of A |  |  |  | 2955.6885
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.5 | 447 | 670.5
1087 | Welder | day | 0.25 | 447 | 111.75
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2 | 368 | 736
| Total of B(1) |  |  |  | 1620
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.4 | 447 | 178.8
1007 | Helper/Khallasi | day | 0.4 | 368 | 147.2
| Total of B(2) |  |  |  | 326
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 1946
| Total of A+B |  |  |  | 4901.6885
| OVERHEADS & PROFIT @ 15 % |  |  |  | 735.25
| Total |  |  |  | 5636.9385
| Rate per metre |  |  |  | 563.6938
| Say |  |  |  | 564
564
Analysis of rate
16.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following thick cross link closed cell preformed sections of polyethylene insulation applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints and repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.2.14 | Chilled water piping of nominal size - 25 mm dia. (19mm thick nitrile rubber insulation) |  | DSR | Rate Rs. | 463
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3014 | M.S. Pipe - 25 mm dia (C-Class) | Mtr | 10 | 156.59 | 1565.9
| add for wastage @ 5% |  |  |  | 78.295
| Total of (A1) |  |  |  | 1644.195
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 246.6293
| Total of (A1 + A2) |  |  |  | 1890.8243
A(3) Basic Price of
4016 | Nitrile rubber (cross link closed cell preformed sections of polyethylene) Insulation -19 mm thickness dia pipe | Sqmtr | 0.9 | 371.8 | 334.62
| add for wastage @ 10% |  |  |  | 33.462
| Total of (A3) |  |  |  | 368.082
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A4) |  |  |  | 0
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 2258.9062
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 22.5891
| Total of A |  |  |  | 2281.4953
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1087 | Welder | day | 0.25 | 447 | 111.75
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 1.75 | 368 | 644
| Total of B(1) |  |  |  | 1416.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.4 | 447 | 178.8
1007 | Helper/Khallasi | day | 0.4 | 368 | 147.2
| Total of B(2) |  |  |  | 326
B(3) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(3) |  |  |  | 0
| Total of B |  |  |  | 1742.25
| Total of A+B |  |  |  | 4023.7453
| OVERHEADS & PROFIT @ 15 % |  |  |  | 603.56
| Total |  |  |  | 4627.3053
| Rate per metre |  |  |  | 462.7305
| Say |  |  |  | 463
463
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.1 | Chilled water piping of nominal size - 400 mm dia. (75mm thick expanded polystrene) |  | DSR | Rate Rs. | 9497
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3001 | M.S. Pipe - 400 mm dia. (Heavy Class, 7 mm thick MS Sheet) | Mtr | 10 | 5040.63 | 50406.3
| add for wastage @ 5% |  |  |  | 2520.315
| Total of (A1) |  |  |  | 52926.615
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 7938.9923
| Total of (A1 + A2) |  |  |  | 60865.6073
A(3) Basic Price of
4017 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -75mm thickness for 400 mm dia pipe | Mtr | 10 | 852.64 | 8526.4
| add for wastage @ 10% |  |  |  | 852.64
| Total of (A3) |  |  |  | 9379.04
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 17.28 | 300 | 5184
| add for wastage @ 10% |  |  |  | 518.4
| Total of (A4) |  |  |  | 5702.4
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 75947.0473
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 759.4705
| Total of A |  |  |  | 76706.5177
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 3 | 447 | 1341
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 4.75 | 368 | 1748
| Total of B(1) |  |  |  | 3841.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(3) |  |  |  | 1018.75
| Total of B |  |  |  | 5878.75
| Total of A+B |  |  |  | 82585.2677
| OVERHEADS & PROFIT @ 15 % |  |  |  | 12387.79
| Total |  |  |  | 94973.0577
| Rate per metre |  |  |  | 9497.3058
| Say |  |  |  | 9497
9497
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.2 | Chilled water piping of nominal size - 350 mm dia. (75mm thick expanded polystrene) |  | DSR | Rate Rs. | 6374
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3002 | M.S. Pipe - 350 mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2955.02 | 29550.2
| add for wastage @ 5% |  |  |  | 1477.51
| Total of (A1) |  |  |  | 31027.71
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 4654.1565
| Total of (A1 + A2) |  |  |  | 35681.8665
A(3) Basic Price of
4018 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -75mm thickness for 350 mm dia pipe | Mtr | 10 | 744.66 | 7446.6
| add for wastage @ 10% |  |  |  | 744.66
| Total of (A3) |  |  |  | 8191.26
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 15.71 | 300 | 4713
| add for wastage @ 10% |  |  |  | 471.3
| Total of (A4) |  |  |  | 5184.3
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 49057.4265
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 490.5743
| Total of A |  |  |  | 49548.0008
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 3 | 447 | 1341
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 4.75 | 368 | 1748
| Total of B(1) |  |  |  | 3841.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(3) |  |  |  | 1018.75
| Total of B |  |  |  | 5878.75
| Total of A+B |  |  |  | 55426.7508
| OVERHEADS & PROFIT @ 15 % |  |  |  | 8314.01
| Total |  |  |  | 63740.7608
| Rate per metre |  |  |  | 6374.0761
| Say |  |  |  | 6374
6374
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.3 | Chilled water piping of nominal size - 300 mm dia. (75mm thick expanded polystrene) |  | DSR | Rate Rs. | 5810
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3003 | M.S. Pipe- 300 mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2673.41 | 26734.1
| add for wastage @ 5% |  |  |  | 1336.705
| Total of (A1) |  |  |  | 28070.805
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 4210.6208
| Total of (A1 + A2) |  |  |  | 32281.4258
A(3) Basic Price of
4019 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -75mm thickness for 300mm dia pipe | Mtr | 10 | 659.02 | 6590.2
| add for wastage @ 10% |  |  |  | 659.02
| Total of (A3) |  |  |  | 7249.22
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 14.14 | 300 | 4242
| add for wastage @ 10% |  |  |  | 424.2
| Total of (A4) |  |  |  | 4666.2
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 44196.8458
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 441.9685
| Total of A |  |  |  | 44638.8142
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 3 | 447 | 1341
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.75 | 407 | 305.25
1007 | Khallasi | day | 4.75 | 368 | 1748
| Total of B(1) |  |  |  | 3841.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(3) |  |  |  | 1018.75
| Total of B |  |  |  | 5878.75
| Total of A+B |  |  |  | 50517.5642
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7577.63
| Total |  |  |  | 58095.1942
| Rate per metre |  |  |  | 5809.5194
| Say |  |  |  | 5810
5810
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.4 | Chilled water piping of nominal size - 250 mm dia. (75mm thick expanded polystrene) |  | DSR | Rate Rs. | 4928
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3004 | M.S. Pipe - 250mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2249.1 | 22491
| add for wastage @ 5% |  |  |  | 1124.55
| Total of (A1) |  |  |  | 23615.55
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 3542.3325
| Total of (A1 + A2) |  |  |  | 27157.8825
A(3) Basic Price of
4020 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -75mm thickness for 250 mm dia pipe | Mtr | 10 | 572.46 | 5724.6
| add for wastage @ 10% |  |  |  | 572.46
| Total of (A3) |  |  |  | 6297.06
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 12.568 | 300 | 3770.4
| add for wastage @ 10% |  |  |  | 377.04
| Total of (A4) |  |  |  | 4147.44
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 37602.3825
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 376.0238
| Total of A |  |  |  | 37978.4063
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 4 | 368 | 1472
| Total of B(1) |  |  |  | 3240
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(2) |  |  |  | 815
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(3) |  |  |  | 815
| Total of B |  |  |  | 4870
| Total of A+B |  |  |  | 42848.4063
| OVERHEADS & PROFIT @ 15 % |  |  |  | 6427.26
| Total |  |  |  | 49275.6663
| Rate per metre |  |  |  | 4927.5666
| Say |  |  |  | 4928
4928
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.5 | Chilled water piping of nominal size - 200 mm dia. (75mm thick expanded polystrene) |  | DSR | Rate Rs. | 4120
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3005 | M.S. Pipe - 200mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 1792.67 | 17926.7
| add for wastage @ 5% |  |  |  | 896.335
| Total of (A1) |  |  |  | 18823.035
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 2823.4552
| Total of (A1 + A2) |  |  |  | 21646.4902
A(3) Basic Price of
4021 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -75 mm thickness for 200 mm dia pipe | Mtr | 10 | 488.68 | 4886.8
| add for wastage @ 10% |  |  |  | 488.68
| Total of (A3) |  |  |  | 5375.48
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 11 | 300 | 3300
| add for wastage @ 10% |  |  |  | 330
| Total of (A4) |  |  |  | 3630
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 30651.9702
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 306.5197
| Total of A |  |  |  | 30958.49
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 4 | 368 | 1472
| Total of B(1) |  |  |  | 3240
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(2) |  |  |  | 815
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(3) |  |  |  | 815
| Total of B |  |  |  | 4870
| Total of A+B |  |  |  | 35828.49
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5374.27
| Total |  |  |  | 41202.76
| Rate per metre |  |  |  | 4120.276
| Say |  |  |  | 4120
4120
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.6 | Chilled water piping of nominal size - 150 mm dia. (75mm thick expanded polystrene) |  | DSR | Rate Rs. | 2779
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3006 | M.S. Pipe - 150mm dia. (C-Class) | Mtr | 10 | 1138.54 | 11385.4
| add for wastage @ 5% |  |  |  | 569.27
| Total of (A1) |  |  |  | 11954.67
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 1793.2005
| Total of (A1 + A2) |  |  |  | 13747.8705
A(3) Basic Price of
4022 | Expanded polystrene moulded pipe section 0/ density 20kg/cum Insulation -75 mm thickness for 150 mm dia pipe | Mtr | 10 | 241.08 | 2410.8
| add for wastage @ 10% |  |  |  | 241.08
| Total of (A3) |  |  |  | 2651.88
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 9.426 | 300 | 2827.8
| add for wastage @ 10% |  |  |  | 282.78
| Total of (A4) |  |  |  | 3110.58
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 19510.3305
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 195.1033
| Total of A |  |  |  | 19705.4338
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 1 | 447 | 447
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 3.5 | 368 | 1288
| Total of B(1) |  |  |  | 2832.5
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(2) |  |  |  | 815
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total of B(3) |  |  |  | 815
| Total of B |  |  |  | 4462.5
| Total of A+B |  |  |  | 24167.9338
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3625.19
| Total |  |  |  | 27793.1238
| Rate per metre |  |  |  | 2779.3124
| Say |  |  |  | 2779
2779
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.7 | Chilled water piping of nominal size - 125 mm dia. (50mm thick expanded polystrene) |  | DSR | Rate Rs. | 2330
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3007 | M.S. Pipe - 125mm dia. (C-Class) | Mtr | 10 | 958.28 | 9582.8
| add for wastage @ 5% |  |  |  | 479.14
| Total of (A1) |  |  |  | 10061.94
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 1509.291
| Total of (A1 + A2) |  |  |  | 11571.231
A(3) Basic Price of
4023 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 125 mm dia pipe | Mtr | 10 | 213.16 | 2131.6
| add for wastage @ 10% |  |  |  | 213.16
| Total of (A3) |  |  |  | 2344.76
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 7.07 | 300 | 2121
| add for wastage @ 10% |  |  |  | 212.1
| Total of (A4) |  |  |  | 2333.1
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 16249.091
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 162.4909
| Total of A |  |  |  | 16411.5819
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 0.75 | 447 | 335.25
1006 | Painter | day | 0.5 | 407 | 203.5
1007 | Khallasi | day | 3.25 | 368 | 1196
| Total of B(1) |  |  |  | 2628.75
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(2) |  |  |  | 611.25
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(3) |  |  |  | 611.25
| Total of B |  |  |  | 3851.25
| Total of A+B |  |  |  | 20262.8319
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3039.42
| Total |  |  |  | 23302.2519
| Rate per metre |  |  |  | 2330.2252
| Say |  |  |  | 2330
2330
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.8 | Chilled water piping of nominal size - 100 mm dia. (50mm thick expanded polystrene) |  | DSR | Rate Rs. | 1981
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3008 | M.S. Pipe - 100mm dia. (C-Class) | Mtr | 10 | 776.98 | 7769.8
| add for wastage @ 5% |  |  |  | 388.49
| Total of (A1) |  |  |  | 8158.29
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 1223.7435
| Total of (A1 + A2) |  |  |  | 9382.0335
A(3) Basic Price of
4024 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 100 mm dia pipe | Mtr | 10 | 179.65 | 1796.5
| add for wastage @ 10% |  |  |  | 179.65
| Total of (A3) |  |  |  | 1976.15
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 6.284 | 300 | 1885.2
| add for wastage @ 10% |  |  |  | 188.52
| Total of (A4) |  |  |  | 2073.72
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 13431.9035
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 134.319
| Total of A |  |  |  | 13566.2225
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 0.75 | 447 | 335.25
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 3 | 368 | 1104
| Total of B(1) |  |  |  | 2435
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(2) |  |  |  | 611.25
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(3) |  |  |  | 611.25
| Total of B |  |  |  | 3657.5
| Total of A+B |  |  |  | 17223.7225
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2583.56
| Total |  |  |  | 19807.2825
| Rate per metre |  |  |  | 1980.7283
| Say |  |  |  | 1981
1981
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.9 | Chilled water piping of nominal size - 80 mm dia. (50mm thick expanded polystrene) |  | DSR | Rate Rs. | 1555
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3009 | M.S. Pipe - 80mm dia. (C-Class) | Mtr | 10 | 527.4 | 5274
| add for wastage @ 5% |  |  |  | 263.7
| Total of (A1) |  |  |  | 5537.7
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 830.655
| Total of (A1 + A2) |  |  |  | 6368.355
A(3) Basic Price of
4025 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 80 mm dia pipe | Mtr | 10 | 157.31 | 1573.1
| add for wastage @ 10% |  |  |  | 157.31
| Total of (A3) |  |  |  | 1730.41
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 5.656 | 300 | 1696.8
| add for wastage @ 10% |  |  |  | 169.68
| Total of (A4) |  |  |  | 1866.48
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 9965.245
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 99.6524
| Total of A |  |  |  | 10064.8974
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.75 | 368 | 1012
| Total of B(1) |  |  |  | 2231.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(2) |  |  |  | 611.25
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(3) |  |  |  | 611.25
| Total of B |  |  |  | 3453.75
| Total of A+B |  |  |  | 13518.6474
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2027.8
| Total |  |  |  | 15546.4474
| Rate per metre |  |  |  | 1554.6447
| Say |  |  |  | 1555
1555
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.10 | Chilled water piping of nominal size - 65 mm dia. (50mm thick expanded polystrene) |  | DSR | Rate Rs. | 1343
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3010 | M.S. Pipe -65mm dia. (C-Class) | Mtr | 10 | 435.46 | 4354.6
| add for wastage @ 5% |  |  |  | 217.73
| Total of (A1) |  |  |  | 4572.33
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 685.8495
| Total of (A1 + A2) |  |  |  | 5258.1795
A(3) Basic Price of
4026 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness -or 65 mm dia pipe | Mtr | 10 | 143.35 | 1433.5
| add for wastage @ 10% |  |  |  | 143.35
| Total of (A3) |  |  |  | 1576.85
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 5.184 | 300 | 1555.2
| add for wastage @ 10% |  |  |  | 155.52
| Total of (A4) |  |  |  | 1710.72
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 8545.7495
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 85.4575
| Total of A |  |  |  | 8631.207
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.75 | 368 | 1012
| Total of B(1) |  |  |  | 2231.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(3) |  |  |  | 407.5
| Total of B |  |  |  | 3046.25
| Total of A+B |  |  |  | 11677.457
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1751.62
| Total |  |  |  | 13429.077
| Rate per metre |  |  |  | 1342.9077
| Say |  |  |  | 1343
1343
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.11 | Chilled water piping of nominal size - 50 mm dia. (50mm thick expanded polystrene) |  | DSR | Rate Rs. | 1109
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3011 | M.S. Pipe -50 mm dia. (C-Class) | Mtr | 10 | 332.26 | 3322.6
| add for wastage @ 5% |  |  |  | 166.13
| Total of (A1) |  |  |  | 3488.73
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 523.3095
| Total of (A1 + A2) |  |  |  | 4012.0395
A(3) Basic Price of
4027 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 50 mm dia pipe | Mtr | 10 | 124.73 | 1247.3
| add for wastage @ 10% |  |  |  | 124.73
| Total of (A3) |  |  |  | 1372.03
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 4.713 | 300 | 1413.9
| add for wastage @ 10% |  |  |  | 141.39
| Total of (A4) |  |  |  | 1555.29
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 6939.3595
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 69.3936
| Total of A |  |  |  | 7008.7531
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.5 | 447 | 670.5
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.25 | 368 | 828
| Total of B(1) |  |  |  | 1823.75
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(3) |  |  |  | 407.5
| Total of B |  |  |  | 2638.75
| Total of A+B |  |  |  | 9647.5031
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1447.13
| Total |  |  |  | 11094.6331
| Rate per metre |  |  |  | 1109.4633
| Say |  |  |  | 1109
1109
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.12 | Chilled water piping of nominal size - 40 mm dia. (50mm thick expanded polystrene) |  | DSR | Rate Rs. | 944
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3012 | M.S. Pipe - 40 mm dia. (C-Class) | Mtr | 10 | 234.64 | 2346.4
| add for wastage @ 5% |  |  |  | 117.32
| Total of (A1) |  |  |  | 2463.72
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 369.558
| Total of (A1 + A2) |  |  |  | 2833.278
A(3) Basic Price of
4028 | Expanded polystrene rnoulded pipe section of density 20kg/cum Insulation -50 mm thickness for 40 mm dia pipe | Mtr | 10 | 111.7 | 1117
| add for wastage @ 10% |  |  |  | 111.7
| Total of (A3) |  |  |  | 1228.7
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 4.399 | 300 | 1319.7
| add for wastage @ 10% |  |  |  | 131.97
| Total of (A4) |  |  |  | 1451.67
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 5513.648
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 55.1365
| Total of A |  |  |  | 5568.7845
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.5 | 447 | 670.5
1087 | Welder | day | 0.5 | 447 | 223.5
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 2.25 | 368 | 828
| Total of B(1) |  |  |  | 1823.75
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(3) |  |  |  | 407.5
| Total of B |  |  |  | 2638.75
| Total of A+B |  |  |  | 8207.5345
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1231.13
| Total |  |  |  | 9438.6645
| Rate per metre |  |  |  | 943.8664
| Say |  |  |  | 944
944
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.13 | Chilled water piping of nominal size - 32 mm dia. (50mm thick expanded polystrene) |  | DSR | Rate Rs. | 834
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3013 | M.S. Pipe - 32 mm dia (C-Class) | Mtr | 10 | 201.71 | 2017.1
| add for wastage @ 5% |  |  |  | 100.855
| Total of (A1) |  |  |  | 2117.955
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 317.6932
| Total of (A1 + A2) |  |  |  | 2435.6482
A(3) Basic Price of
4029 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 32 mm dia pipe | Mtr | 10 | 106.11 | 1061.1
| add for wastage @ 10% |  |  |  | 106.11
| Total of (A3) |  |  |  | 1167.21
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 4.147 | 300 | 1244.1
| add for wastage @ 10% |  |  |  | 124.41
| Total of (A4) |  |  |  | 1368.51
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 4971.3682
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 49.7137
| Total of A |  |  |  | 5021.0819
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1087 | Welder | day | 0.25 | 447 | 111.75
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 1.75 | 368 | 644
| Total of B(1) |  |  |  | 1416.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(3) |  |  |  | 407.5
| Total of B |  |  |  | 2231.25
| Total of A+B |  |  |  | 7252.3319
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1087.85
| Total |  |  |  | 8340.1819
| Rate per metre |  |  |  | 834.0182
| Say |  |  |  | 834
834
Analysis of rate
16.3 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping plumbing inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystyrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. Note : The Pipes of sizes 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.3.14 | Chilled water piping of nominal size - 25 mm dia. (50mm thick expanded polystrene) |  | DSR | Rate Rs. | 749
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3014 | M.S. Pipe - 25 mm dia (C-Class) | Mtr | 10 | 156.59 | 1565.9
| add for wastage @ 5% |  |  |  | 78.295
| Total of (A1) |  |  |  | 1644.195
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-insulators and fitting such as bends, tees etc. @ 15% |  |  |  | 246.6293
| Total of (A1 + A2) |  |  |  | 1890.8243
A(3) Basic Price of
4030 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 25 mm dia pipe | Mtr | 10 | 95.87 | 958.7
| add for wastage @ 10% |  |  |  | 95.87
| Total of (A3) |  |  |  | 1054.57
A(4) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 3.928 | 300 | 1178.4
| add for wastage @ 10% |  |  |  | 117.84
| Total of (A4) |  |  |  | 1296.24
| Total of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 4241.6343
| add for cartage @ 1% of (A(1)+A(2)+A(3)+A(4)) |  |  |  | 42.4163
| Total of A |  |  |  | 4284.0506
LABOUR
B(1) For Piping work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1087 | Welder | day | 0.25 | 447 | 111.75
1006 | Painter | day | 0.25 | 407 | 101.75
1007 | Khallasi | day | 1.75 | 368 | 644
| Total of B(1) |  |  |  | 1416.25
B(2) For Insulation work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(2) |  |  |  | 407.5
B(3) For Cadding work
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total of B(3) |  |  |  | 407.5
| Total of B |  |  |  | 2231.25
| Total of A+B |  |  |  | 6515.3006
| OVERHEADS & PROFIT @ 15 % |  |  |  | 977.3
| Total |  |  |  | 7492.6006
| Rate per metre |  |  |  | 749.2601
| Say |  |  |  | 749
749
Analysis of rate
16.4 | Supplying, laying/ fixing, testing and commissioning of following thickness resin bonded fiber glass pipe section insulation having density 80 kg/cum duly covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) on existing pipe and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints etc. as per specifications and as required.
16.4.1 | Resin bonded fiber glass insulation of thickness 65 mm on existing pipe |  | DSR | Rate Rs. | 2038
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
4031 | Resin bonded fiber glass insulation of thickness 65 mm on existing pipe | Sqmtr | 10 | 1111.87 | 11118.7
| add for wastage @ 10% |  |  |  | 1111.87
| Total of (A1) |  |  |  | 12230.57
A(2) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 10 | 300 | 3000
| add for wastage @ 10% |  |  |  | 300
| Total of (A2) |  |  |  | 3300
| Total of (A(1)+A(2)) |  |  |  | 15530.57
| add for cartage @ 1% of (A(1)+A(2)) |  |  |  | 155.3057
| Total of A |  |  |  | 15685.8757
LABOUR
B(1) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(1) |  |  |  | 1018.75
B(2) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
| Total of B |  |  |  | 2037.5
| Total of A+B |  |  |  | 17723.3757
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2658.51
| Total |  |  |  | 20381.8857
| Rate per sq metre |  |  |  | 2038.1886
| Say |  |  |  | 2038
2038
Analysis of rate
16.4 | Supplying, laying/ fixing, testing and commissioning of following thickness resin bonded fiber glass pipe section insulation having density 80 kg/cum duly covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) on existing pipe and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints etc. as per specifications and as required.
16.4.2 | Resin bonded fiber glass insulation of thickness 50 mm on existing pipe |  | DSR | Rate Rs. | 1784
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
4032 | Resin bonded fiber glass insulation of thickness 50 mm on existing pipe | Sqmtr | 10 | 912.63 | 9126.3
| add for wastage @ 10% |  |  |  | 912.63
| Total of (A1) |  |  |  | 10038.93
A(2) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 10 | 300 | 3000
| add for wastage @ 10% |  |  |  | 300
| Total of (A2) |  |  |  | 3300
| Total of (A(1)+A(2)) |  |  |  | 13338.93
| add for cartage @ 1% of (A(1)+A(2)) |  |  |  | 133.3893
| Total of A |  |  |  | 13472.3193
LABOUR
B(1) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(1) |  |  |  | 1018.75
B(2) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
| Total of B |  |  |  | 2037.5
| Total of A+B |  |  |  | 15509.8193
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2326.47
| Total |  |  |  | 17836.2893
| Rate per sq metre |  |  |  | 1783.6289
| Say |  |  |  | 1784
1784
Analysis of rate
16.4 | Supplying, laying/ fixing, testing and commissioning of following thickness resin bonded fiber glass pipe section insulation having density 80 kg/cum duly covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) on existing pipe and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints etc. as per specifications and as required.
16.4.3 | Resin bonded fiber glass insulation of thickness 40 mm on existing pipe |  | DSR | Rate Rs. | 1685
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
4033 | Resin bonded fiber glass insulation of thickness 40 mm on existing pipe | Sqmtr | 10 | 835.51 | 8355.1
| add for wastage @ 10% |  |  |  | 835.51
| Total of (A1) |  |  |  | 9190.61
A(2) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 10 | 300 | 3000
| add for wastage @ 10% |  |  |  | 300
| Total of (A2) |  |  |  | 3300
| Total of (A(1)+A(2)) |  |  |  | 12490.61
| add for cartage @ 1% of (A(1)+A(2)) |  |  |  | 124.9061
| Total of A |  |  |  | 12615.5161
LABOUR
B(1) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(1) |  |  |  | 1018.75
B(2) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
| Total of B |  |  |  | 2037.5
| Total of A+B |  |  |  | 14653.0161
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2197.95
| Total |  |  |  | 16850.9661
| Rate per sq metre |  |  |  | 1685.0966
| Say |  |  |  | 1685
1685
Analysis of rate
16.4 | Supplying, laying/ fixing, testing and commissioning of following thickness resin bonded fiber glass pipe section insulation having density 80 kg/cum duly covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) on existing pipe and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints etc. as per specifications and as required.
16.4.4 | Resin bonded fiber glass insulation of thickness 25 mm on existing pipe |  | DSR | Rate Rs. | 1439
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
4034 | Resin bonded fiber glass insulation of thickness 25 mm on existing pipe | Sqmtr | 10 | 642.7 | 6427
| add for wastage @ 10% |  |  |  | 642.7
| Total of (A1) |  |  |  | 7069.7
A(2) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 10 | 300 | 3000
| add for wastage @ 10% |  |  |  | 300
| Total of (A2) |  |  |  | 3300
| Total of (A(1)+A(2)) |  |  |  | 10369.7
| add for cartage @ 1% of (A(1)+A(2)) |  |  |  | 103.697
| Total of A |  |  |  | 10473.397
LABOUR
B(1) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(1) |  |  |  | 1018.75
B(2) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
| Total of B |  |  |  | 2037.5
| Total of A+B |  |  |  | 12510.897
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1876.63
| Total |  |  |  | 14387.527
| Rate per sq metre |  |  |  | 1438.7527
| Say |  |  |  | 1439
1439
Analysis of rate
16.5 | Supplying, laying/ fixing, testing and commissioning of following thickness cross link closed cell preformed sections of polyethylene insulation Nitrile rubber applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints etc. as per specifications and as required complete in all respect.
16.5.1 | Insulation with nitrile rubber of thickness 32mm on existing pipe |  | DSR | Rate Rs. | 911
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
4015 | Nitrile rubber (cross link closed cell preformed sections dia polyethylene) Insulation -32 mm thickness dia pipe | Sqmtr | 10 | 658.35 | 6583.5
| add for wastage @ 10% |  |  |  | 658.35
| Total of (A1) |  |  |  | 7241.85
A(2) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A2) |  |  |  | 0
| Total of (A(1)+A(2)) |  |  |  | 7241.85
| add for cartage @ 1% of (A(1)+A(2)) |  |  |  | 72.4185
| Total of A |  |  |  | 7314.2685
LABOUR
B(1) For Insulation work
1004 | Fitter, Grade 1 | day | 0.75 | 447 | 335.25
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
| Total of B(1) |  |  |  | 611.25
B(2) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(2) |  |  |  | 0
| Total of B |  |  |  | 611.25
| Total of A+B |  |  |  | 7925.5185
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1188.83
| Total |  |  |  | 9114.3485
| Rate per sq metre |  |  |  | 911.4348
| Say |  |  |  | 911
911
Analysis of rate
16.5 | Supplying, laying/ fixing, testing and commissioning of following thickness cross link closed cell preformed sections of polyethylene insulation Nitrile rubber applied by adhesive confirming to standard specifications and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints etc. as per specifications and as required complete in all respect.
16.5.2 | Insulation with nitrile rubber of thickness 19mm on existing pipe |  | DSR | Rate Rs. | 536
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
4016 | Nitrile rubber (cross link closed cell preformed sections of polyethylene) Insulation -19 mm thickness dia pipe | Sqmtr | 10 | 371.8 | 3718
| add for wastage @ 10% |  |  |  | 371.8
| Total of (A1) |  |  |  | 4089.8
A(2) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr |  | 300 | 0
| add for wastage @ 10% |  |  |  | 0
| Total of (A2) |  |  |  | 0
| Total of (A(1)+A(2)) |  |  |  | 4089.8
| add for cartage @ 1% of (A(1)+A(2)) |  |  |  | 40.898
| Total of A |  |  |  | 4130.698
LABOUR
B(1) For Insulation work
1004 | Fitter, Grade 1 | day | 0.65 | 447 | 290.55
1007 | Helper/Khallasi | day | 0.65 | 368 | 239.2
| Total of B(1) |  |  |  | 529.75
B(2) For Cadding work
1004 | Fitter, Grade 1 | day |  | 447 | 0
1007 | Helper/Khallasi | day |  | 368 | 0
| Total of B(2) |  |  |  | 0
| Total of B |  |  |  | 529.75
| Total of A+B |  |  |  | 4660.448
| OVERHEADS & PROFIT @ 15 % |  |  |  | 699.07
| Total |  |  |  | 5359.518
| Rate per sq metre |  |  |  | 535.9518
| Say |  |  |  | 536
536
Analysis of rate
16.6 | Supplying, laying/ fixing, testing and commissioning of following thickness insulation with fire retardant quality expanded polystrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing etc. as per specifications and as required complete in all respect.
16.6.1 | Insulation with expanded polystrene of thickness 75mm on existing pipe |  | DSR | Rate Rs. | 1512
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
4037 | Expanded polystrene insulation pipe of thickness 75 mm on existing pipe | Sqmtr | 10 | 699.98 | 6999.8
| add for wastage @ 10% |  |  |  | 699.98
| Total of (A1) |  |  |  | 7699.78
A(2) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 10 | 300 | 3000
| add for wastage @ 10% |  |  |  | 300
| Total of (A2) |  |  |  | 3300
| Total of (A(1)+A(2)) |  |  |  | 10999.78
| add for cartage @ 1% of (A(1)+A(2)) |  |  |  | 109.9978
| Total of A |  |  |  | 11109.7778
LABOUR
B(1) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(1) |  |  |  | 1018.75
B(2) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
| Total of B |  |  |  | 2037.5
| Total of A+B |  |  |  | 13147.2778
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1972.09
| Total |  |  |  | 15119.3678
| Rate per sq metre |  |  |  | 1511.9368
| Say |  |  |  | 1512
1512
Analysis of rate
16.6 | Supplying, laying/ fixing, testing and commissioning of following thickness insulation with fire retardant quality expanded polystrene moulded pipe section of density 20 kg/cum after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessian and finally applying 0.63mm aluminium sheet cladding complete with type 3, grade 1 roofing feltstrip (as per IS:1322 as amended up to date) at joints repairing etc. as per specifications and as required complete in all respect.
16.6.2 | Insulation with expanded polystrene of thickness 50mm on existing pipe |  | DSR | Rate Rs. | 1137
Details of cost for 10 metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
4038 | Expanded polystrene insulation pipe of thickness 50 mm on existing pipe | Sqmtr | 10 | 446.8 | 4468
| add for wastage @ 10% |  |  |  | 446.8
| Total of (A1) |  |  |  | 4914.8
A(2) Basic Price of
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 10 | 300 | 3000
| add for wastage @ 10% |  |  |  | 300
| Total of (A2) |  |  |  | 3300
| Total of (A(1)+A(2)) |  |  |  | 8214.8
| add for cartage @ 1% of (A(1)+A(2)) |  |  |  | 82.148
| Total of A |  |  |  | 8296.948
LABOUR
B(1) For Insulation work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(1) |  |  |  | 1018.75
B(2) For Cadding work
1004 | Fitter, Grade 1 | day | 1.25 | 447 | 558.75
1007 | Helper/Khallasi | day | 1.25 | 368 | 460
| Total of B(2) |  |  |  | 1018.75
| Total of B |  |  |  | 2037.5
| Total of A+B |  |  |  | 10334.448
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1550.17
| Total |  |  |  | 11884.618
| Rate per sq metre |  |  |  | 1188.4618
| Say |  |  |  | 1188
1188
Analysis of rate
16.7
16.7.1 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Butterfly valve (Manual) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water/hot water circulation as specified.
16.7.1.1 | Butterfly valve (Manual) 200 mm |  | DSR | Rate Rs. | 11102
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3024 | 200 mm dia | Each | 1 | 8330 | 8330
| Total (A) |  |  |  | 8330
B (INSULATION)
Basic Price of
4021 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -75 mm thickness for 200 mm dia pipe | Mtr | 0.3 | 488.68 | 146.6
| add for wastage @ 10% |  |  |  | 14.66
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.3 | 300 | 90
| add for wastage @ 10% |  |  |  | 9
| Total (B) |  |  |  | 260.26
| Total (A+B) |  |  |  | 8590.26
| add for cartage @ 1% on (A+B) |  |  |  | 85.9026
| Total |  |  |  | 8676.1626
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.7 | 368 | 257.6
For Insulation
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
For Cadding
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
| Total of (B) |  |  |  | 978
| Total of A+B+C |  |  |  | 9654.1626
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1448.12
| Total |  |  |  | 11102.2826
| Rate per each |  |  |  | 11102.2826
| Say |  |  |  | 11102
11102
Analysis of rate
16.7.1 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Butterfly valve (Manual) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water/hot water circulation as specified.
16.7.1.2 | Butterfly valve (Manual) 150 mm |  | DSR | Rate Rs. | 6625
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3025 | 150mm dia. | Each | 1 | 4536 | 4536
| Total (A) |  |  |  | 4536
B (INSULATION)
Basic Price of
4022 | Expanded polystrene moulded pipe section 0/ density 20kg/cum Insulation -75 mm thickness for 150 mm dia pipe | Mtr | 0.3 | 241.08 | 72.32
| add for wastage @ 10% |  |  |  | 7.232
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.24 | 300 | 72
| add for wastage @ 10% |  |  |  | 7.2
| Total (B) |  |  |  | 158.752
| Total (A+B) |  |  |  | 4694.752
| add for cartage @ 1% on (A+B) |  |  |  | 46.9475
| Total |  |  |  | 4741.6995
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
For Insulation
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
For Cadding
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
| Total of (B) |  |  |  | 1018.75
| Total of A+B+C |  |  |  | 5760.4495
| OVERHEADS & PROFIT @ 15 % |  |  |  | 864.07
| Total |  |  |  | 6624.5195
| Rate per each |  |  |  | 6624.5195
| Say |  |  |  | 6625
6625
Analysis of rate
16.7.1 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Butterfly valve (Manual) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water/hot water circulation as specified.
16.7.1.3 | Butterfly valve (Manual) 125 mm |  | DSR | Rate Rs. | 5780
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3026 | 125mm dia. | Each | 1 | 3864 | 3864
| add for cartage @ 1% |  |  |  | 38.64
| Total (A) |  |  |  | 3902.64
B (INSULATION)
Basic Price of
4027 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 50 mm dia pipe | Mtr | 0.3 | 124.73 | 37.42
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.19 | 300 | 57
| Total |  |  |  | 94.42
| add for wastage @ 10% |  |  |  | 9.442
| Total |  |  |  | 103.862
| add for cartage @ 1% |  |  |  | 1.0386
| Total (B) |  |  |  | 104.9006
| Total (A+B) |  |  |  | 4007.5406
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
For Insulation
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
For Cadding
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
| Total of (B) |  |  |  | 1018.75
| Total of A+B+C |  |  |  | 5026.2906
| OVERHEADS & PROFIT @ 15 % |  |  |  | 753.94
| Total |  |  |  | 5780.2306
| Rate per each |  |  |  | 5780.2306
| Say |  |  |  | 5780
5780
Analysis of rate
16.7.1 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Butterfly valve (Manual) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water/hot water circulation as specified.
16.7.1.4 | Butterfly valve (Manual) 100 mm |  | DSR | Rate Rs. | 5330
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3027 | 100mm dia. | Each | 1 | 3465 | 3465
| add for cartage @ 1% |  |  |  | 34.65
| Total (A) |  |  |  | 3499.65
B (INSULATION)
Basic Price of
4024 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 100 mm dia pipe | Mtr | 0.3 | 179.65 | 53.9
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.17 | 300 | 51
| Total |  |  |  | 104.9
| add for wastage @ 10% |  |  |  | 10.49
| Total |  |  |  | 115.39
| add for cartage @ 1% |  |  |  | 1.1539
| Total (B) |  |  |  | 116.5439
| Total (A+B) |  |  |  | 3616.1939
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
For Insulation
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
For Cadding
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
| Total of (B) |  |  |  | 1018.75
| Total of A+B+C |  |  |  | 4634.9439
| OVERHEADS & PROFIT @ 15 % |  |  |  | 695.24
| Total |  |  |  | 5330.1839
| Rate per each |  |  |  | 5330.1839
| Say |  |  |  | 5330
5330
Analysis of rate
16.7.1 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Butterfly valve (Manual) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water/hot water circulation as specified.
16.7.1.5 | Butterfly valve (Manual) 80 mm |  | DSR | Rate Rs. | 3719
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3028 | 80mm dia. | Each | 1 | 2469.6 | 2469.6
| add for cartage @ 1% |  |  |  | 24.696
| Total (A) |  |  |  | 2494.296
B (INSULATION)
Basic Price of
4025 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 80 mm dia pipe | Mtr | 0.2 | 157.31 | 31.46
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.12 | 300 | 36
| Total |  |  |  | 67.46
| add for wastage @ 10% |  |  |  | 6.746
| Total |  |  |  | 74.206
| add for cartage @ 1% |  |  |  | 0.74206
| Total (B) |  |  |  | 74.9481
| Total (A+B) |  |  |  | 2569.2441
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1087 | Welder | day | 0.21 | 447 | 93.87
1007 | Helper/Khallasi | day | 0.47 | 368 | 172.96
For Insulation
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
For Cadding
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
| Total of (B) |  |  |  | 663.83
| Total of A+B+C |  |  |  | 3233.0741
| OVERHEADS & PROFIT @ 15 % |  |  |  | 484.96
| Total |  |  |  | 3718.0341
| Rate per each |  |  |  | 3718.0341
| Say |  |  |  | 3718
3718
Analysis of rate
16.7.1 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Butterfly valve (Manual) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water/hot water circulation as specified.
16.7.1.6 | Butterfly valve (Manual) 65 mm |  | DSR | Rate Rs. | 3351
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3029 | 65mm dia. | Each | 1 | 2175.6 | 2175.6
| add for cartage @ 1% |  |  |  | 21.756
| Total (A) |  |  |  | 2197.356
B (INSULATION)
Basic Price of
4026 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness -or 65 mm dia pipe | Mtr | 0.2 | 143.35 | 28.67
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.07 | 300 | 21
| Total |  |  |  | 49.67
| add for wastage @ 10% |  |  |  | 4.967
| Total |  |  |  | 54.637
| add for cartage @ 1% |  |  |  | 0.54637
| Total (B) |  |  |  | 55.1834
| Total (A+B) |  |  |  | 2252.5394
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1087 | Welder | day | 0.21 | 447 | 93.87
1007 | Helper/Khallasi | day | 0.46 | 368 | 169.28
For Insulation
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
For Cadding
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
| Total of (B) |  |  |  | 660.15
| Total of A+B+C |  |  |  | 2912.6894
| OVERHEADS & PROFIT @ 15 % |  |  |  | 436.9
| Total |  |  |  | 3349.5894
| Rate per each |  |  |  | 3349.5894
| Say |  |  |  | 3350
3350
Analysis of rate
16.7.1 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Butterfly valve (Manual) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water/hot water circulation as specified.
16.7.1.7 | Butterfly valve (Manual) 50 mm |  | DSR | Rate Rs. | 3050
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3030 | 50mm dia. | Each | 1 | 1999.2 | 1999.2
| add for cartage @ 1% |  |  |  | 19.992
| Total (A) |  |  |  | 2019.192
B (INSULATION)
Basic Price of
4027 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 50 mm dia pipe | Mtr | 0.2 | 124.73 | 24.95
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.06 | 300 | 18
| Total |  |  |  | 42.95
| add for wastage @ 10% |  |  |  | 4.295
| Total |  |  |  | 47.245
| add for cartage @ 1% |  |  |  | 0.47245
| Total (B) |  |  |  | 47.7175
| Total (A+B) |  |  |  | 2066.9095
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1087 | Welder | day | 0.17 | 447 | 75.99
1007 | Helper/Khallasi | day | 0.37 | 368 | 136.16
For Insulation
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
For Cadding
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
| Total of (B) |  |  |  | 586.8
| Total of A+B+C |  |  |  | 2653.7095
| OVERHEADS & PROFIT @ 15 % |  |  |  | 398.06
| Total |  |  |  | 3051.7695
| Rate per each |  |  |  | 3051.7695
| Say |  |  |  | 3052
3052
Analysis of rate
16.7.1 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Butterfly valve (Manual) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water/hot water circulation as specified.
16.7.1.8 | Butterfly valve (Manual) 40 mm |  | DSR | Rate Rs. | 2686
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3031 | 40mm dia. | Each | 1 | 1808 | 1808
| add for cartage @ 1% |  |  |  | 18.08
| Total (A) |  |  |  | 1826.08
B (INSULATION)
Basic Price of
4028 | Expanded polystrene rnoulded pipe section of density 20kg/cum Insulation -50 mm thickness for 40 mm dia pipe | Mtr | 0.2 | 111.7 | 22.34
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.06 | 300 | 18
| Total |  |  |  | 40.34
| add for wastage @ 10% |  |  |  | 4.034
| Total |  |  |  | 44.374
| add for cartage @ 1% |  |  |  | 0.44374
| Total (B) |  |  |  | 44.8177
| Total (A+B) |  |  |  | 1870.8977
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1087 | Welder | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.3 | 368 | 110.4
For Insulation
1004 | Fitter, Grade 1 | day | 0.12 | 447 | 53.64
1007 | Helper/Khallasi | day | 0.12 | 368 | 44.16
For Cadding
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
| Total of (B) |  |  |  | 464.55
| Total of A+B+C |  |  |  | 2335.4477
| OVERHEADS & PROFIT @ 15 % |  |  |  | 350.32
| Total |  |  |  | 2685.7677
| Rate per each |  |  |  | 2685.7677
| Say |  |  |  | 2686
2686
Analysis of rate
16.7
16.7.2 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Balancing valve with built in measuring facility with C I body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified.
16.7.2.1 | Balancing valve with built in measuring facility mm |  | DSR | Rate Rs. | 48763
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3032 | 200 mm dia | Each | 1 | 40857.6 | 40857.6
| add for cartage @ 1% |  |  |  | 408.576
| Total (A) |  |  |  | 41266.176
B (INSULATION)
Basic Price of
4021 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -75 mm thickness for 200 mm dia pipe | Mtr | 0.3 | 488.68 | 146.6
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.28 | 300 | 84
| Total |  |  |  | 230.6
| add for wastage @ 10% |  |  |  | 23.06
| Total |  |  |  | 253.66
| add for cartage @ 1% |  |  |  | 2.5366
| Total (B) |  |  |  | 256.1966
| Total (A+B) |  |  |  | 41522.3726
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.48 | 447 | 214.56
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.68 | 368 | 250.24
For Insulation
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
For Cadding
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
| Total of (B) |  |  |  | 880.2
| Total of A+B+C |  |  |  | 42402.5726
| OVERHEADS & PROFIT @ 15 % |  |  |  | 6360.39
| Total |  |  |  | 48762.9626
| Rate per each |  |  |  | 48762.9626
| Say |  |  |  | 48763
48763
Analysis of rate
16.7
16.7.2 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Balancing valve with built in measuring facility with C I body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified.
16.7.2.2 | Balancing valve with built in measuring facility mm |  | DSR | Rate Rs. | 23798
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3033 | 150mm dia. | Each | 1 | 19491.15 | 19491.15
| add for cartage @ 1% |  |  |  | 194.9115
| Total (A) |  |  |  | 19686.0615
B (INSULATION)
Basic Price of
4022 | Expanded polystrene moulded pipe section 0/ density 20kg/cum Insulation -75 mm thickness for 150 mm dia pipe | Mtr | 0.3 | 241.08 | 72.32
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.24 | 300 | 72
| Total |  |  |  | 144.32
| add for wastage @ 10% |  |  |  | 14.432
| Total |  |  |  | 158.752
| add for cartage @ 1% |  |  |  | 1.5875
| Total (B) |  |  |  | 160.3395
| Total (A+B) |  |  |  | 19846.401
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.48 | 447 | 214.56
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.68 | 368 | 250.24
For Insulation
1004 | Fitter, Grade 1 | day | 0.19 | 447 | 84.93
1007 | Helper/Khallasi | day | 0.19 | 368 | 69.92
For Cadding
1004 | Fitter, Grade 1 | day | 0.18 | 447 | 80.46
1007 | Helper/Khallasi | day | 0.18 | 368 | 66.24
| Total of (B) |  |  |  | 855.75
| Total of A+B+C |  |  |  | 20702.151
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3105.32
| Total |  |  |  | 23807.471
| Rate per each |  |  |  | 23807.471
| Say |  |  |  | 23807
23807
Analysis of rate
16.7
16.7.2 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Balancing valve with built in measuring facility with C I body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified.
16.7.2.3 | Balancing valve with built in measuring facility mm |  | DSR | Rate Rs. | 18608
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3034 | 125mm dia. | Each | 1 | 13027.35 | 13027.35
| add for cartage @ 1% |  |  |  | 130.2735
| Total (A) |  |  |  | 13157.6235
B (INSULATION)
Basic Price of
4023 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 125 mm dia pipe | Mtr | 0.3 | 213.16 | 63.95
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.19 | 300 | 57
| Total |  |  |  | 120.95
| add for wastage @ 10% |  |  |  | 12.095
| Total |  |  |  | 133.045
| add for cartage @ 1% |  |  |  | 1.3305
| Total (B) |  |  |  | 134.3755
| Total (A+B) |  |  |  | 13291.9989
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.48 | 447 | 214.56
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.69 | 368 | 253.92
For Insulation
1004 | Fitter, Grade 1 | day | 0.19 | 447 | 84.93
1007 | Helper/Khallasi | day | 0.19 | 368 | 69.92
For Cadding
1004 | Fitter, Grade 1 | day | 0.18 | 447 | 80.46
1007 | Helper/Khallasi | day | 0.18 | 368 | 66.24
| Total of (B) |  |  |  | 859.43
| Total of A+B+C |  |  |  | 14151.4289
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2122.71
| Total |  |  |  | 16274.139
| Rate per each |  |  |  | 16274.139
| Say |  |  |  | 16274
16274
Analysis of rate
16.7
16.7.2 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Balancing valve with built in measuring facility with C I body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified.
16.7.2.4 | Balancing valve with built in measuring facility mm |  | DSR | Rate Rs. | 11945
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3035 | 100mm dia. | Each | 1 | 9301.69 | 9301.69
| add for cartage @ 1% |  |  |  | 93.0169
| Total (A) |  |  |  | 9394.7069
B (INSULATION)
Basic Price of
4024 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 100 mm dia pipe | Mtr | 0.35 | 179.65 | 62.88
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.17 | 300 | 51
| Total |  |  |  | 113.88
| add for wastage @ 10% |  |  |  | 11.388
| Total |  |  |  | 125.268
| add for cartage @ 1% |  |  |  | 1.2527
| Total (B) |  |  |  | 126.5207
| Total (A+B) |  |  |  | 9521.2276
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.48 | 447 | 214.56
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.68 | 368 | 250.24
For Insulation
1004 | Fitter, Grade 1 | day | 0.19 | 447 | 84.93
1007 | Helper/Khallasi | day | 0.19 | 368 | 69.92
For Cadding
1004 | Fitter, Grade 1 | day | 0.18 | 447 | 80.46
1007 | Helper/Khallasi | day | 0.18 | 368 | 66.24
| Total of (B) |  |  |  | 855.75
| Total of A+B+C |  |  |  | 10376.9776
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1556.55
| Total |  |  |  | 11933.5276
| Rate per each |  |  |  | 11933.5276
| Say |  |  |  | 11934
11934
Analysis of rate
16.7
16.7.2 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Balancing valve with built in measuring facility with C I body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified.
16.7.2.5 | Balancing valve with built in measuring facility mm |  | DSR | Rate Rs. | 7395
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3036 | 80mm dia. | Each | 1 | 5675.78 | 5675.78
| add for cartage @ 1% |  |  |  | 56.7578
| Total (A) |  |  |  | 5732.5378
B (INSULATION)
Basic Price of
4025 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 80 mm dia pipe | Mtr | 0.2 | 157.31 | 31.46
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.12 | 300 | 36
| Total |  |  |  | 67.46
| add for wastage @ 10% |  |  |  | 6.746
| Total |  |  |  | 74.206
| add for cartage @ 1% |  |  |  | 0.74206
| Total (B) |  |  |  | 74.9481
| Total (A+B) |  |  |  | 5807.4859
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.26 | 447 | 116.22
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.46 | 368 | 169.28
For Insulation
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
For Cadding
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
| Total of (B) |  |  |  | 619.4
| Total of A+B+C |  |  |  | 6426.8859
| OVERHEADS & PROFIT @ 15 % |  |  |  | 964.03
| Total |  |  |  | 7390.9159
| Rate per each |  |  |  | 7390.9159
| Say |  |  |  | 7391
7391
Analysis of rate
16.7
16.7.2 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Balancing valve with built in measuring facility with C I body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified.
16.7.2.6 | Balancing valve with built in measuring facility mm |  | DSR | Rate Rs. | 7101
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3037 | 65 mm dia | Each | 1 | 5436.38 | 5436.38
| add for cartage @ 1% |  |  |  | 54.3638
| Total (A) |  |  |  | 5490.7438
B (INSULATION)
Basic Price of
4026 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness -or 65 mm dia pipe | Mtr | 0.2 | 143.35 | 28.67
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.07 | 300 | 21
| Total |  |  |  | 49.67
| add for wastage @ 10% |  |  |  | 4.967
| Total |  |  |  | 54.637
| add for cartage @ 1% |  |  |  | 0.54637
| Total (B) |  |  |  | 55.1834
| Total (A+B) |  |  |  | 5545.9272
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.26 | 447 | 116.22
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.47 | 368 | 172.96
For Insulation
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
For Cadding
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
| Total of (B) |  |  |  | 623.08
| Total of A+B+C |  |  |  | 6169.0072
| OVERHEADS & PROFIT @ 15 % |  |  |  | 925.35
| Total |  |  |  | 7094.3572
| Rate per each |  |  |  | 7094.3572
| Say |  |  |  | 7094
7094
Analysis of rate
16.7
16.7.2 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Balancing valve with built in measuring facility with C I body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified.
16.7.2.7 | Balancing valve with built in measuring facility mm |  | DSR | Rate Rs. | 6386
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3038 | 50mm dia. | Each | 1 | 4887.75 | 4887.75
| add for cartage @ 1% |  |  |  | 48.8775
| Total (A) |  |  |  | 4936.6275
B (INSULATION)
Basic Price of
4027 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 50 mm dia pipe | Mtr | 0.2 | 124.73 | 24.95
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.07 | 300 | 21
| Total |  |  |  | 45.95
| add for wastage @ 10% |  |  |  | 4.595
| Total |  |  |  | 50.545
| add for cartage @ 1% |  |  |  | 0.50545
| Total (B) |  |  |  | 51.0505
| Total (A+B) |  |  |  | 4987.6779
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.4 | 368 | 147.2
For Insulation
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
For Cadding
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
| Total of (B) |  |  |  | 570.5
| Total of A+B+C |  |  |  | 5558.1779
| OVERHEADS & PROFIT @ 15 % |  |  |  | 833.73
| Total |  |  |  | 6391.9079
| Rate per each |  |  |  | 6391.9079
| Say |  |  |  | 6392
6392
Analysis of rate
16.7
16.7.2 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Balancing valve with built in measuring facility with C I body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified.
16.7.2.8 | Balancing valve with built in measuring facility mm |  | DSR | Rate Rs. | 3175
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3039 | 40 mm dia | Each | 1 | 2236 | 2236
| add for cartage @ 1% |  |  |  | 22.36
| Total (A) |  |  |  | 2258.36
B (INSULATION)
Basic Price of
4028 | Expanded polystrene rnoulded pipe section of density 20kg/cum Insulation -50 mm thickness for 40 mm dia pipe | Mtr | 0.2 | 111.7 | 22.34
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.06 | 300 | 18
| Total |  |  |  | 40.34
| add for wastage @ 10% |  |  |  | 4.034
| Total |  |  |  | 44.374
| add for cartage @ 1% |  |  |  | 0.44374
| Total (B) |  |  |  | 44.8177
| Total (A+B) |  |  |  | 2303.1777
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.14 | 447 | 62.58
1087 | Welder | day | 0.14 | 447 | 62.58
1007 | Helper/Khallasi | day | 0.28 | 368 | 103.04
For Insulation
1004 | Fitter, Grade 1 | day | 0.14 | 447 | 62.58
1007 | Helper/Khallasi | day | 0.14 | 368 | 51.52
For Cadding
1004 | Fitter, Grade 1 | day | 0.14 | 447 | 62.58
1007 | Helper/Khallasi | day | 0.14 | 368 | 51.52
| Total of (B) |  |  |  | 456.4
| Total of A+B+C |  |  |  | 2759.5777
| OVERHEADS & PROFIT @ 15 % |  |  |  | 413.94
| Total |  |  |  | 3173.5177
| Rate per each |  |  |  | 3173.5177
| Say |  |  |  | 3174
3174
Analysis of rate
16.7
16.7.3 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. NON - RETURN VALVE with duel plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating for chilled/ hot water circulation including insulation as specified.
16.7.3.1 | Non - return valve of 200 mm dia |  | DSR | Rate Rs. | 9655
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3040 | 200 mm dia | Each | 1 | 7052.33 | 7052.33
| add for cartage @ 1% |  |  |  | 70.5233
| Total (A) |  |  |  | 7122.8533
B (INSULATION)
Basic Price of
4021 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -75 mm thickness for 200 mm dia pipe | Mtr | 0.3 | 488.68 | 146.6
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.28 | 300 | 84
| Total |  |  |  | 230.6
| add for wastage @ 10% |  |  |  | 23.06
| Total |  |  |  | 253.66
| add for cartage @ 1% |  |  |  | 2.5366
| Total (B) |  |  |  | 256.1966
| Total (A+B) |  |  |  | 7379.0499
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
For Insulation
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
For Cadding
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
| Total of (B) |  |  |  | 1018.75
| Total of A+B+C |  |  |  | 8397.7999
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1259.67
| Total |  |  |  | 9657.4699
| Rate per each |  |  |  | 9657.4699
| Say |  |  |  | 9657
9657
Analysis of rate
16.7
16.7.3 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. NON - RETURN VALVE with duel plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating for chilled/ hot water circulation including insulation as specified.
16.7.3.2 | Non - return valve of 150 mm dia |  | DSR | Rate Rs. | 6477
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3041 | 150mm dia. | Each | 1 | 4428.9 | 4428.9
| add for cartage @ 1% |  |  |  | 44.289
| Total (A) |  |  |  | 4473.189
B (INSULATION)
Basic Price of
4022 | Expanded polystrene moulded pipe section 0/ density 20kg/cum Insulation -75 mm thickness for 150 mm dia pipe | Mtr | 0.3 | 241.08 | 72.32
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.24 | 300 | 72
| Total |  |  |  | 144.32
| add for wastage @ 10% |  |  |  | 14.432
| Total |  |  |  | 158.752
| add for cartage @ 1% |  |  |  | 1.5875
| Total (B) |  |  |  | 160.3395
| Total (A+B) |  |  |  | 4633.5285
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.23 | 447 | 102.81
1007 | Helper/Khallasi | day | 0.73 | 368 | 268.64
For Insulation
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1007 | Helper/Khallasi | day | 0.25 | 368 | 92
For Cadding
1004 | Fitter, Grade 1 | day | 0.24 | 447 | 107.28
1007 | Helper/Khallasi | day | 0.24 | 368 | 88.32
| Total of (B) |  |  |  | 994.3
| Total of A+B+C |  |  |  | 5627.8285
| OVERHEADS & PROFIT @ 15 % |  |  |  | 844.17
| Total |  |  |  | 6471.9985
| Rate per each |  |  |  | 6471.9985
| Say |  |  |  | 6472
6472
Analysis of rate
16.7
16.7.3 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. NON - RETURN VALVE with duel plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating for chilled/ hot water circulation including insulation as specified.
16.7.3.3 | Non - return valve of 125 mm dia |  | DSR | Rate Rs. | 5163
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3042 | 125mm dia. | Each | 1 | 3361.58 | 3361.58
| add for cartage @ 1% |  |  |  | 33.6158
| Total (A) |  |  |  | 3395.1958
B (INSULATION)
Basic Price of
4023 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 125 mm dia pipe | Mtr | 0.3 | 213.16 | 63.95
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.19 | 300 | 57
| Total |  |  |  | 120.95
| add for wastage @ 10% |  |  |  | 12.095
| Total |  |  |  | 133.045
| add for cartage @ 1% |  |  |  | 1.3305
| Total (B) |  |  |  | 134.3755
| Total (A+B) |  |  |  | 3529.5712
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.23 | 447 | 102.81
1007 | Helper/Khallasi | day | 0.73 | 368 | 268.64
For Insulation
1004 | Fitter, Grade 1 | day | 0.23 | 447 | 102.81
1007 | Helper/Khallasi | day | 0.23 | 368 | 84.64
For Cadding
1004 | Fitter, Grade 1 | day | 0.22 | 447 | 98.34
1007 | Helper/Khallasi | day | 0.22 | 368 | 80.96
| Total of (B) |  |  |  | 961.7
| Total of A+B+C |  |  |  | 4491.2712
| OVERHEADS & PROFIT @ 15 % |  |  |  | 673.69
| Total |  |  |  | 5164.9613
| Rate per each |  |  |  | 5164.9613
| Say |  |  |  | 5165
5165
Analysis of rate
16.7
16.7.3 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. NON - RETURN VALVE with duel plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating for chilled/ hot water circulation including insulation as specified.
16.7.3.4 | Non - return valve of 100 mm dia |  | DSR | Rate Rs. | 3893
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3043 | 100 mm dia | Each | 1 | 2294.25 | 2294.25
| add for cartage @ 1% |  |  |  | 22.9425
| Total (A) |  |  |  | 2317.1925
B (INSULATION)
Basic Price of
4024 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 100 mm dia pipe | Mtr | 0.3 | 179.65 | 53.9
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.17 | 300 | 51
| Total |  |  |  | 104.9
| add for wastage @ 10% |  |  |  | 10.49
| Total |  |  |  | 115.39
| add for cartage @ 1% |  |  |  | 1.1539
| Total (B) |  |  |  | 116.5439
| Total (A+B) |  |  |  | 2433.7364
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.23 | 447 | 102.81
1007 | Helper/Khallasi | day | 0.73 | 368 | 268.64
For Insulation
1004 | Fitter, Grade 1 | day | 0.22 | 447 | 98.34
1007 | Helper/Khallasi | day | 0.22 | 368 | 80.96
For Cadding
1004 | Fitter, Grade 1 | day | 0.22 | 447 | 98.34
1007 | Helper/Khallasi | day | 0.22 | 368 | 80.96
| Total of (B) |  |  |  | 953.55
| Total of A+B+C |  |  |  | 3387.2864
| OVERHEADS & PROFIT @ 15 % |  |  |  | 508.09
| Total |  |  |  | 3895.3764
| Rate per each |  |  |  | 3895.3764
| Say |  |  |  | 3895
3895
Analysis of rate
16.7
16.7.3 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. NON - RETURN VALVE with duel plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating for chilled/ hot water circulation including insulation as specified.
16.7.3.5 | Non - return valve of 80 mm dia |  | DSR | Rate Rs. | 2811
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3044 | 80mm dia. | Each | 1 | 1680.79 | 1680.79
| add for cartage @ 1% |  |  |  | 16.8079
| Total (A) |  |  |  | 1697.5979
B (INSULATION)
Basic Price of
4025 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 80 mm dia pipe | Mtr | 0.2 | 157.31 | 31.46
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.12 | 300 | 36
| Total |  |  |  | 67.46
| add for wastage @ 10% |  |  |  | 6.746
| Total |  |  |  | 74.206
| add for cartage @ 1% |  |  |  | 0.74206
| Total (B) |  |  |  | 74.9481
| Total (A+B) |  |  |  | 1772.546
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.45 | 368 | 165.6
For Insulation
1004 | Fitter, Grade 1 | day | 0.18 | 447 | 80.46
1007 | Helper/Khallasi | day | 0.18 | 368 | 66.24
For Cadding
1004 | Fitter, Grade 1 | day | 0.19 | 447 | 84.93
1007 | Helper/Khallasi | day | 0.19 | 368 | 69.92
| Total of (B) |  |  |  | 668.3
| Total of A+B+C |  |  |  | 2440.846
| OVERHEADS & PROFIT @ 15 % |  |  |  | 366.13
| Total |  |  |  | 2806.976
| Rate per each |  |  |  | 2806.976
| Say |  |  |  | 2807
2807
Analysis of rate
16.7
16.7.3 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. NON - RETURN VALVE with duel plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating for chilled/ hot water circulation including insulation as specified.
16.7.3.6 | Non - return valve of 65 mm dia |  | DSR | Rate Rs. | 2443
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3045 | 65 mm dia | Each | 1 | 1386.53 | 1386.53
| add for cartage @ 1% |  |  |  | 13.8653
| Total (A) |  |  |  | 1400.3953
B (INSULATION)
Basic Price of
4026 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness -or 65 mm dia pipe | Mtr | 0.2 | 143.35 | 28.67
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.07 | 300 | 21
| Total |  |  |  | 49.67
| add for wastage @ 10% |  |  |  | 4.967
| Total |  |  |  | 54.637
| add for cartage @ 1% |  |  |  | 0.54637
| Total (B) |  |  |  | 55.1834
| Total (A+B) |  |  |  | 1455.5787
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.45 | 368 | 165.6
For Insulation
1004 | Fitter, Grade 1 | day | 0.18 | 447 | 80.46
1007 | Helper/Khallasi | day | 0.18 | 368 | 66.24
For Cadding
1004 | Fitter, Grade 1 | day | 0.19 | 447 | 84.93
1007 | Helper/Khallasi | day | 0.19 | 368 | 69.92
| Total of (B) |  |  |  | 668.3
| Total of A+B+C |  |  |  | 2123.8787
| OVERHEADS & PROFIT @ 15 % |  |  |  | 318.58
| Total |  |  |  | 2442.4587
| Rate per each |  |  |  | 2442.4587
| Say |  |  |  | 2442
2442
Analysis of rate
16.7
16.7.4 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Y - Strainer of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified.
16.7.4.1 | Y - Strainer of 200 mm dia |  | DSR | Rate Rs. | 20853
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3046 | 200mm dia | Each | 1 | 16794.91 | 16794.91
| add for cartage @ 1% |  |  |  | 167.9491
| Total (A) |  |  |  | 16962.8591
B (INSULATION)
Basic Price of
4021 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -75 mm thickness for 200 mm dia pipe | Mtr | 0.3 | 488.68 | 146.6
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.283 | 300 | 84.9
| Total |  |  |  | 231.5
| add for wastage @ 10% |  |  |  | 23.15
| Total |  |  |  | 254.65
| add for cartage @ 1% |  |  |  | 2.5465
| Total (B) |  |  |  | 257.1965
| Total (A+B) |  |  |  | 17220.0556
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.7 | 368 | 257.6
For Insulation
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
For Cadding
1004 | Fitter, Grade 1 | day | 0.22 | 447 | 98.34
1007 | Helper/Khallasi | day | 0.22 | 368 | 80.96
| Total of (B) |  |  |  | 912.8
| Total of A+B+C |  |  |  | 18132.8556
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2719.93
| Total |  |  |  | 20852.7856
| Rate per each |  |  |  | 20852.7856
| Say |  |  |  | 20853
20853
Analysis of rate
16.7
16.7.4 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Y - Strainer of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified.
16.7.4.2 | Y - Strainer of 150 mm dia |  | DSR | Rate Rs. | 10530
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3047 | 150mm dia. | Each | 1 | 8002.94 | 8002.94
| add for cartage @ 1% |  |  |  | 80.0294
| Total (A) |  |  |  | 8082.9694
B (INSULATION)
Basic Price of
4022 | Expanded polystrene moulded pipe section 0/ density 20kg/cum Insulation -75 mm thickness for 150 mm dia pipe | Mtr | 0.3 | 241.08 | 72.32
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.24 | 300 | 72
| Total |  |  |  | 144.32
| add for wastage @ 10% |  |  |  | 14.432
| Total |  |  |  | 158.752
| add for cartage @ 1% |  |  |  | 1.5875
| Total (B) |  |  |  | 160.3395
| Total (A+B) |  |  |  | 8243.3089
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.75 | 368 | 276
For Insulation
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
For Cadding
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
| Total of (B) |  |  |  | 914.9
| Total of A+B+C |  |  |  | 9158.2089
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1373.73
| Total |  |  |  | 10531.9389
| Rate per each |  |  |  | 10531.9389
| Say |  |  |  | 10532
10532
Analysis of rate
16.7
16.7.4 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Y - Strainer of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified.
16.7.4.3 | Y - Strainer of 125 mm dia |  | DSR | Rate Rs. | 9880
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3048 | 125mm dia. | Each | 1 | 7496.21 | 7496.21
| add for cartage @ 1% |  |  |  | 74.9621
| Total (A) |  |  |  | 7571.1721
B (INSULATION)
Basic Price of
4023 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 125 mm dia pipe | Mtr | 0.3 | 213.16 | 63.95
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.19 | 300 | 57
| Total |  |  |  | 120.95
| add for wastage @ 10% |  |  |  | 12.095
| Total |  |  |  | 133.045
| add for cartage @ 1% |  |  |  | 1.3305
| Total (B) |  |  |  | 134.3755
| Total (A+B) |  |  |  | 7705.5476
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.71 | 368 | 261.28
For Insulation
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
For Cadding
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
| Total of (B) |  |  |  | 900.18
| Total of A+B+C |  |  |  | 8605.7275
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1290.86
| Total |  |  |  | 9896.5876
| Rate per each |  |  |  | 9896.5876
| Say |  |  |  | 9897
9897
Analysis of rate
16.7
16.7.4 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Y - Strainer of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified.
16.7.4.4 | Y - Strainer of 100 mm dia |  | DSR | Rate Rs. | 6918
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3049 | 100 mm dia | Each | 1 | 4937.63 | 4937.63
| add for cartage @ 1% |  |  |  | 49.3763
| Total (A) |  |  |  | 4987.0063
B (INSULATION)
Basic Price of
4024 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 100 mm dia pipe | Mtr | 0.3 | 179.65 | 53.9
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.17 | 300 | 51
| Total |  |  |  | 104.9
| add for wastage @ 10% |  |  |  | 10.49
| Total |  |  |  | 115.39
| add for cartage @ 1% |  |  |  | 1.1539
| Total (B) |  |  |  | 116.5439
| Total (A+B) |  |  |  | 5103.5502
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.71 | 368 | 261.28
For Insulation
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
For Cadding
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
| Total of (B) |  |  |  | 900.18
| Total of A+B+C |  |  |  | 6003.7302
| OVERHEADS & PROFIT @ 15 % |  |  |  | 900.56
| Total |  |  |  | 6904.2902
| Rate per each |  |  |  | 6904.2902
| Say |  |  |  | 6904
6904
Analysis of rate
16.7
16.7.4 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Y - Strainer of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified.
16.7.4.5 | Y - Strainer of 100 mm dia |  | DSR | Rate Rs. | 5026
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3050 | 80 mm dia | Each | 1 | 3620.93 | 3620.93
| add for cartage @ 1% |  |  |  | 36.2093
| Total (A) |  |  |  | 3657.1393
B (INSULATION)
Basic Price of
4025 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 80 mm dia pipe | Mtr | 0.2 | 157.31 | 31.46
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.12 | 300 | 36
| Total |  |  |  | 67.46
| add for wastage @ 10% |  |  |  | 6.746
| Total |  |  |  | 74.206
| add for cartage @ 1% |  |  |  | 0.74206
| Total (B) |  |  |  | 74.9481
| Total (A+B) |  |  |  | 3732.0874
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.45 | 368 | 165.6
For Insulation
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
For Cadding
1004 | Fitter, Grade 1 | day | 0.18 | 447 | 80.46
1007 | Helper/Khallasi | day | 0.18 | 368 | 66.24
| Total of (B) |  |  |  | 635.7
| Total of A+B+C |  |  |  | 4367.7874
| OVERHEADS & PROFIT @ 15 % |  |  |  | 655.17
| Total |  |  |  | 5022.9574
| Rate per each |  |  |  | 5022.9574
| Say |  |  |  | 5023
5023
Analysis of rate
16.7
16.7.4 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Y - Strainer of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified.
16.7.4.6 | Y - Strainer of 65 mm dia |  | DSR | Rate Rs. | 4434
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3051 | 65mm dia. | Each | 1 | 3127.16 | 3127.16
| add for cartage @ 1% |  |  |  | 31.2716
| Total (A) |  |  |  | 3158.4316
B (INSULATION)
Basic Price of
4026 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness -or 65 mm dia pipe | Mtr | 0.2 | 143.35 | 28.67
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.07 | 300 | 21
| Total |  |  |  | 49.67
| add for wastage @ 10% |  |  |  | 4.967
| Total |  |  |  | 54.637
| add for cartage @ 1% |  |  |  | 0.54637
| Total (B) |  |  |  | 55.1834
| Total (A+B) |  |  |  | 3213.615
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.25 | 447 | 111.75
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.46 | 368 | 169.28
For Insulation
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
For Cadding
1004 | Fitter, Grade 1 | day | 0.18 | 447 | 80.46
1007 | Helper/Khallasi | day | 0.18 | 368 | 66.24
| Total of (B) |  |  |  | 639.38
| Total of A+B+C |  |  |  | 3852.995
| OVERHEADS & PROFIT @ 15 % |  |  |  | 577.95
| Total |  |  |  | 4430.945
| Rate per each |  |  |  | 4430.945
| Say |  |  |  | 4431
4431
Analysis of rate
16.7
16.7.4 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Y - Strainer of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified.
16.7.4.7 | Y - Strainer of 65 mm dia |  | DSR | Rate Rs. | 3516
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3052 | 50mm dia. | Each | 1 | 2413.95 | 2413.95
| add for cartage @ 1% |  |  |  | 24.1395
| Total (A) |  |  |  | 2438.0895
B (INSULATION)
Basic Price of
4027 | Expanded polystrene moulded pipe section of density 20kg/cum Insulation -50 mm thickness for 50 mm dia pipe | Mtr | 0.2 | 124.73 | 24.95
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.06 | 300 | 18
| Total |  |  |  | 42.95
| add for wastage @ 10% |  |  |  | 4.295
| Total |  |  |  | 47.245
| add for cartage @ 1% |  |  |  | 0.47245
| Total (B) |  |  |  | 47.7175
| Total (A+B) |  |  |  | 2485.807
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.4 | 368 | 147.2
For Insulation
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
For Cadding
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
| Total of (B) |  |  |  | 570.5
| Total of A+B+C |  |  |  | 3056.307
| OVERHEADS & PROFIT @ 15 % |  |  |  | 458.45
| Total |  |  |  | 3514.7569
| Rate per each |  |  |  | 3514.7569
| Say |  |  |  | 3515
3515
Analysis of rate
16.7
16.7.4 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications. Y - Strainer of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified.
16.7.4.8 | Y - Strainer of 65 mm dia |  | DSR | Rate Rs. | 2478
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3053 | 40mm dia. | Each | 1 | 1645.88 | 1645.88
| add for cartage @ 1% |  |  |  | 16.4588
| Total (A) |  |  |  | 1662.3388
B (INSULATION)
Basic Price of
4028 | Expanded polystrene rnoulded pipe section of density 20kg/cum Insulation -50 mm thickness for 40 mm dia pipe | Mtr | 0.2 | 111.7 | 22.34
3023 | Pipe aluminium Cladding 0.63mm/Valve Cladding | Mtr | 0.06 | 300 | 18
| Total |  |  |  | 40.34
| add for wastage @ 10% |  |  |  | 4.034
| Total |  |  |  | 44.374
| add for cartage @ 1% |  |  |  | 0.44374
| Total (B) |  |  |  | 44.8177
| Total (A+B) |  |  |  | 1707.1565
C (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1087 | Welder | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.3 | 368 | 110.4
For Insulation
1004 | Fitter, Grade 1 | day | 0.14 | 447 | 62.58
1007 | Helper/Khallasi | day | 0.14 | 368 | 51.52
For Cadding
1004 | Fitter, Grade 1 | day | 0.11 | 447 | 49.17
1007 | Helper/Khallasi | day | 0.11 | 368 | 40.48
| Total of (B) |  |  |  | 448.25
| Total of A+B+C |  |  |  | 2155.4065
| OVERHEADS & PROFIT @ 15 % |  |  |  | 323.31
| Total |  |  |  | 2478.7165
| Rate per each |  |  |  | 2478.7165
| Say |  |  |  | 2479
2479
Analysis of rate
16.8 | Providing and fixing in position the industrial type pressure gauge complete as required.
|  |  | DSR | Rate Rs. | 973
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
(A) MATERIAL
Basic Price
3054 | Industrial type pressure gauges with gun metal / brass valves | Each | 1 | 717 | 717
| add for cartage @ 1% |  |  |  | 7.17
| Total A |  |  |  | 724.17
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.15 | 368 | 55.2
| Total (B) |  |  |  | 122.25
| Total of (A+B) |  |  |  | 846.42
| OVERHEADS & PROFIT @ 15 % |  |  |  | 126.96
| Total |  |  |  | 973.38
| Rate per each |  |  |  | 973.38
| Say |  |  |  | 973
973
Analysis of rate
16.9 | Providing and fixing in position the industrial type pressure gauge complete as required.
|  |  | DSR | Rate Rs. | 707
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
(A) MATERIAL
Basic Price
3055 | Industrial type thermometers. | Each | 1 | 525 | 525
| add packing, forwarding and fright etc. @ 1% |  |  |  | 5.25
| Total A |  |  |  | 530.25
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.1 | 447 | 44.7
1007 | Helper/Khallasi | day | 0.1 | 368 | 36.8
| Total (B) |  |  |  | 81.5
| Total of (A+B) |  |  |  | 611.75
| OVERHEADS & PROFIT @ 15 % |  |  |  | 91.76
| Total |  |  |  | 703.51
| Rate per each |  |  |  | 703.51
| Say |  |  |  | 704
704
Analysis of rate
16.10 | Condenser water pipe
16.10.1 | Supplying, fixing, testing and commissioning of condenser water pipes of following sizes of MS ‘C’ class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted/buried in ground excavation and refilling etc. as per specification and as required complete in all respect. Note:-The Pipes size 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.10.1.1 | Condenser water pipe of nominal size - 300mm dia |  | DSR | Rate Rs. | 4187
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3003 | M.S. Pipe- 300 mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2673.41 | 26734.1
| add for wastage @ 5% |  |  |  | 1336.705
| Total of (A1) |  |  |  | 28070.805
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-isolators and fittingssuch as bends, tees etc. @ 15% |  |  |  | 4210.6208
| Total of (A1) + (A2) |  |  |  | 32281.4258
| add for cartage etc. @ 1% of (A1) + (A2) |  |  |  | 322.8143
| Total of A |  |  |  | 32604.24
B (LABOUR)
For piping work
1004 | Fitter, Grade 1 | day | 3 | 447 | 1341
1087 | Welder | day | 0.95 | 447 | 424.65
1006 | Painter | day | 0.75 | 407 | 305.25
1007 | Helper/Khallasi | day | 4.7 | 368 | 1729.6
| Total of (B) |  |  |  | 3800.5
| Total of A+B |  |  |  | 36404.74
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5460.71
| Total |  |  |  | 41865.45
| Rate per metre |  |  |  | 4186.545
| Say |  |  |  | 4187
4187
Analysis of rate
16.10 | Condenser water pipe
16.10.1 | Supplying, fixing, testing and commissioning of condenser water pipes of following sizes of MS ‘C’ class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted/buried in ground excavation and refilling etc. as per specification and as required complete in all respect. Note:-The Pipes size 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.10.1.2 | Condenser water pipe of nominal size - 250mm dia |  | DSR | Rate Rs. | 3524
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3004 | M.S. Pipe - 250mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 2249.1 | 22491
| add for wastage @ 5% |  |  |  | 1124.55
| Total of (A1) |  |  |  | 23615.55
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-isolators and fittingssuch as bends, tees etc. @ 15% |  |  |  | 3542.3325
| Total of (A1) + (A2) |  |  |  | 27157.8825
| add for cartage etc. @ 1% of (A1) + (A2) |  |  |  | 271.5788
| Total of A |  |  |  | 27429.4613
B (LABOUR)
For piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 0.95 | 447 | 424.65
1006 | Painter | day | 0.52 | 407 | 211.64
1007 | Helper/Khallasi | day | 3.97 | 368 | 1460.96
| Total of (B) |  |  |  | 3214.75
| Total of A+B |  |  |  | 30644.2113
| OVERHEADS & PROFIT @ 15 % |  |  |  | 4596.63
| Total |  |  |  | 35240.8413
| Rate per metre |  |  |  | 3524.0841
| Say |  |  |  | 3524
3524
Analysis of rate
16.10 | Condenser water pipe
16.10.1 | Supplying, fixing, testing and commissioning of condenser water pipes of following sizes of MS ‘C’ class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted/buried in ground excavation and refilling etc. as per specification and as required complete in all respect. Note:-The Pipes size 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.10.1.3 | Condenser water pipe of nominal size - 200mm dia |  | DSR | Rate Rs. | 2918
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3005 | M.S. Pipe - 200mm dia. (Heavy Class, 6.35 mm thick MS Sheet) | Mtr | 10 | 1792.67 | 17926.7
| add for wastage @ 5% |  |  |  | 896.335
| Total of (A1) |  |  |  | 18823.035
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-isolators and fittingssuch as bends, tees etc. @ 15% |  |  |  | 2823.4552
| Total of (A1) + (A2) |  |  |  | 21646.4902
| add for cartage etc. @ 1% of (A1) + (A2) |  |  |  | 216.4649
| Total of A |  |  |  | 21862.9552
B (LABOUR)
For piping work
1004 | Fitter, Grade 1 | day | 2.86 | 447 | 1278.42
1087 | Welder | day | 0.95 | 447 | 424.65
1006 | Painter | day | 0.52 | 407 | 211.64
1007 | Helper/Khallasi | day | 4.33 | 368 | 1593.44
| Total of (B) |  |  |  | 3508.15
| Total of A+B |  |  |  | 25371.1052
| OVERHEADS & PROFIT @ 15 % |  |  |  | 3805.67
| Total |  |  |  | 29176.7752
| Rate per metre |  |  |  | 2917.6775
| Say |  |  |  | 2918
2918
Analysis of rate
16.10 | Condenser water pipe
16.10.1 | Supplying, fixing, testing and commissioning of condenser water pipes of following sizes of MS ‘C’ class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted/buried in ground excavation and refilling etc. as per specification and as required complete in all respect. Note:-The Pipes size 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.10.1.4 | Condenser water pipe of nominal size - 150mm dia |  | DSR | Rate Rs. | 1983
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3006 | M.S. Pipe - 150mm dia. (C-Class) | Mtr | 10 | 1138.54 | 11385.4
| add for wastage @ 5% |  |  |  | 569.27
| Total of (A1) |  |  |  | 11954.67
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-isolators and fittingssuch as bends, tees etc. @ 15% |  |  |  | 1793.2005
| Total of (A1) + (A2) |  |  |  | 13747.8705
| add for cartage etc. @ 1% of (A1) + (A2) |  |  |  | 137.4787
| Total of A |  |  |  | 13885.3492
B (LABOUR)
For piping work
1004 | Fitter, Grade 1 | day | 2.68 | 447 | 1197.96
1087 | Welder | day | 0.95 | 447 | 424.65
1006 | Painter | day | 0.52 | 407 | 211.64
1007 | Helper/Khallasi | day | 4.15 | 368 | 1527.2
| Total of (B) |  |  |  | 3361.45
| Total of A+B |  |  |  | 17246.7992
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2587.02
| Total |  |  |  | 19833.8192
| Rate per metre |  |  |  | 1983.3819
| Say |  |  |  | 1983
1983
Analysis of rate
16.10 | Condenser water pipe
16.10.1 | Supplying, fixing, testing and commissioning of condenser water pipes of following sizes of MS ‘C’ class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted/buried in ground excavation and refilling etc. as per specification and as required complete in all respect. Note:-The Pipes size 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.10.1.5 | Condenser water pipe of nominal size - 150mm dia |  | DSR | Rate Rs. | 1710
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3007 | M.S. Pipe - 125mm dia. (C-Class) | Mtr | 10 | 958.28 | 9582.8
| add for wastage @ 5% |  |  |  | 479.14
| Total of (A1) |  |  |  | 10061.94
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-isolators and fittingssuch as bends, tees etc. @ 15% |  |  |  | 1509.291
| Total of (A1) + (A2) |  |  |  | 11571.231
| add for cartage etc. @ 1% of (A1) + (A2) |  |  |  | 115.7123
| Total of A |  |  |  | 11686.9433
B (LABOUR)
For piping work
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1087 | Welder | day | 0.91 | 447 | 406.77
1006 | Painter | day | 0.52 | 407 | 211.64
1007 | Helper/Khallasi | day | 3.93 | 368 | 1446.24
| Total of (B) |  |  |  | 3182.15
| Total of A+B |  |  |  | 14869.0933
| OVERHEADS & PROFIT @ 15 % |  |  |  | 2230.36
| Total |  |  |  | 17099.4533
| Rate per metre |  |  |  | 1709.9453
| Say |  |  |  | 1710
1710
Analysis of rate
16.10 | Condenser water pipe
16.10.1 | Supplying, fixing, testing and commissioning of condenser water pipes of following sizes of MS ‘C’ class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted/buried in ground excavation and refilling etc. as per specification and as required complete in all respect. Note:-The Pipes size 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
16.10.1.6 | Condenser water pipe of nominal size - 150mm dia |  | DSR | Rate Rs. | 1436
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
A(1) Basic Price of
3008 | M.S. Pipe - 100mm dia. (C-Class) | Mtr | 10 | 776.98 | 7769.8
| add for wastage @ 5% |  |  |  | 388.49
| Total of (A1) |  |  |  | 8158.29
| A(2) Add for necessary brackets, supports, saddles, clamps, hangers, vibration-isolators and fittingssuch as bends, tees etc. @ 15% |  |  |  | 1223.7435
| Total of (A1) + (A2) |  |  |  | 9382.0335
| add for cartage etc. @ 1% of (A1) + (A2) |  |  |  | 93.8203
| Total of A |  |  |  | 9475.8538
B (LABOUR)
For piping work
1004 | Fitter, Grade 1 | day | 2.4 | 447 | 1072.8
1087 | Welder | day | 0.8 | 447 | 357.6
1006 | Painter | day | 0.52 | 407 | 211.64
1007 | Helper/Khallasi | day | 3.72 | 368 | 1368.96
| Total of (B) |  |  |  | 3011
| Total of A+B |  |  |  | 12486.8538
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1873.03
| Total |  |  |  | 14359.8838
| Rate per metre |  |  |  | 1435.9884
| Say |  |  |  | 1436
1436
Analysis of rate
16.11
16.11.1 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Butterfly valve (manual) with C I body SS disc nitrile sheet & O-ring & PN 16 pressure rating as specified.
16.11.1.1 | Butterfly valve (manual) 200mm |  | DSR | Rate Rs. | 10261
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3024 | 200 mm dia | Each | 1 | 8330 | 8330
| add for cartage etc. @ 1% |  |  |  | 83.3
| Total A |  |  |  | 8413.3
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.48 | 447 | 214.56
1087 | Welder | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.63 | 368 | 231.84
| Total (B) |  |  |  | 513.45
| Total of (A+B) |  |  |  | 8926.75
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1339.01
| Total |  |  |  | 10265.76
| Rate per each |  |  |  | 10265.76
| Say |  |  |  | 10266
10266
Analysis of rate
16.11
16.11.1 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Butterfly valve (manual) with C I body SS disc nitrile sheet & O-ring & PN 16 pressure rating as specified.
16.11.1.2 | Butterfly valve (manual) 150mm |  | DSR | Rate Rs. | 5914
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3025 | 150mm dia. | Each | 1 | 4536 | 4536
| add for cartage etc. @ 1% |  |  |  | 45.36
| Total A |  |  |  | 4581.36
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.19 | 447 | 84.93
1007 | Helper/Khallasi | day | 0.69 | 368 | 253.92
| Total (B) |  |  |  | 562.35
| Total of (A+B) |  |  |  | 5143.71
| OVERHEADS & PROFIT @ 15 % |  |  |  | 771.56
| Total |  |  |  | 5915.27
| Rate per each |  |  |  | 5915.27
| Say |  |  |  | 5915
5915
Analysis of rate
16.11
16.11.1 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Butterfly valve (manual) with C I body SS disc nitrile sheet & O-ring & PN 16 pressure rating as specified.
16.11.1.3 | Butterfly valve (manual) 125mm |  | DSR | Rate Rs. | 5138
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3026 | 125mm dia. | Each | 1 | 3864 | 3864
| add for cartage etc. @ 1% |  |  |  | 38.64
| Total A |  |  |  | 3902.64
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.19 | 447 | 84.93
1007 | Helper/Khallasi | day | 0.69 | 368 | 253.92
| Total (B) |  |  |  | 562.35
| Total of (A+B) |  |  |  | 4464.99
| OVERHEADS & PROFIT @ 15 % |  |  |  | 669.75
| Total |  |  |  | 5134.74
| Rate per each |  |  |  | 5134.74
| Say |  |  |  | 5135
5135
Analysis of rate
16.11
16.11.1 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Butterfly valve (manual) with C I body SS disc nitrile sheet & O-ring & PN 16 pressure rating as specified.
16.11.1.4 | Butterfly valve (manual) 100mm |  | DSR | Rate Rs. | 4685
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3027 | 100mm dia. | Each | 1 | 3465 | 3465
| add for cartage etc. @ 1% |  |  |  | 34.65
| Total A |  |  |  | 3499.65
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.7 | 368 | 257.6
| Total (B) |  |  |  | 570.5
| Total of (A+B) |  |  |  | 4070.15
| OVERHEADS & PROFIT @ 15 % |  |  |  | 610.52
| Total |  |  |  | 4680.67
| Rate per each |  |  |  | 4680.67
| Say |  |  |  | 4681
4681
Analysis of rate
16.11
16.11.1 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Butterfly valve (manual) with C I body SS disc nitrile sheet & O-ring & PN 16 pressure rating as specified.
16.11.1.5 | Butterfly valve (manual) 80mm |  | DSR | Rate Rs. | 3302
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3028 | 80mm dia. | Each | 1 | 2469.6 | 2469.6
| add for cartage etc. @ 1% |  |  |  | 24.696
| Total A |  |  |  | 2494.296
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.3 | 447 | 134.1
1087 | Welder | day | 0.16 | 447 | 71.52
1007 | Helper/Khallasi | day | 0.46 | 368 | 169.28
| Total (B) |  |  |  | 374.9
| Total of (A+B) |  |  |  | 2869.196
| OVERHEADS & PROFIT @ 15 % |  |  |  | 430.38
| Total |  |  |  | 3299.576
| Rate per each |  |  |  | 3299.576
| Say |  |  |  | 3300
3300
Analysis of rate
16.11
16.11.1 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Butterfly valve (manual) with C I body SS disc nitrile sheet & O-ring & PN 16 pressure rating as specified.
16.11.1.6 | Butterfly valve (manual) 65mm |  | DSR | Rate Rs. | 2971
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3029 | 65mm dia. | Each | 1 | 2175.6 | 2175.6
| add for cartage etc. @ 1% |  |  |  | 21.756
| Total A |  |  |  | 2197.356
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.3 | 447 | 134.1
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total (B) |  |  |  | 407.5
| Total of (A+B) |  |  |  | 2604.856
| OVERHEADS & PROFIT @ 15 % |  |  |  | 390.73
| Total |  |  |  | 2995.586
| Rate per each |  |  |  | 2995.586
| Say |  |  |  | 2996
2996
Analysis of rate
16.11
16.11.1 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Butterfly valve (manual) with C I body SS disc nitrile sheet & O-ring & PN 16 pressure rating as specified.
16.11.1.7 | Butterfly valve (manual) 50mm |  | DSR | Rate Rs. | 2671
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3030 | 50mm dia. | Each | 1 | 1999.2 | 1999.2
| add for cartage etc. @ 1% |  |  |  | 19.992
| Total A |  |  |  | 2019.192
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.22 | 447 | 98.34
1087 | Welder | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.37 | 368 | 136.16
| Total (B) |  |  |  | 301.55
| Total of (A+B) |  |  |  | 2320.742
| OVERHEADS & PROFIT @ 15 % |  |  |  | 348.11
| Total |  |  |  | 2668.852
| Rate per each |  |  |  | 2668.852
| Say |  |  |  | 2669
2669
Analysis of rate
16.11
16.11.1 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Butterfly valve (manual) with C I body SS disc nitrile sheet & O-ring & PN 16 pressure rating as specified.
16.11.1.8 | Butterfly valve (manual) 40mm |  | DSR | Rate Rs. | 2357
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3031 | 40mm dia. | Each | 1 | 1808 | 1808
| add for cartage etc. @ 1% |  |  |  | 18.08
| Total A |  |  |  | 1826.08
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.15 | 447 | 67.05
1087 | Welder | day | 0.12 | 447 | 53.64
1007 | Helper/Khallasi | day | 0.27 | 368 | 99.36
| Total (B) |  |  |  | 220.05
| Total of (A+B) |  |  |  | 2046.13
| OVERHEADS & PROFIT @ 15 % |  |  |  | 306.92
| Total |  |  |  | 2353.05
| Rate per each |  |  |  | 2353.05
| Say |  |  |  | 2353
2353
Analysis of rate
16.11
16.11.2 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Non - Return Valve with dual plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating as specified.
16.11.2.1 | Non - Return Valve of 200mm dia |  | DSR | Rate Rs. | 8805
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3040 | 200 mm dia | Each | 1 | 7052.33 | 7052.33
| add for cartage etc. @ 1% |  |  |  | 70.5233
| Total A |  |  |  | 7122.8533
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.16 | 447 | 71.52
1007 | Helper/Khallasi | day | 0.66 | 368 | 242.88
| Total (B) |  |  |  | 537.9
| Total of (A+B) |  |  |  | 7660.7533
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1149.11
| Total |  |  |  | 8809.8633
| Rate per each |  |  |  | 8809.8633
| Say |  |  |  | 8810
8810
Analysis of rate
16.11
16.11.2 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Non - Return Valve with dual plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating as specified.
16.11.2.2 | Non - Return Valve of 150mm dia |  | DSR | Rate Rs. | 5772
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3041 | 150mm dia. | Each | 1 | 4428.9 | 4428.9
| add for cartage etc. @ 1% |  |  |  | 44.289
| Total A |  |  |  | 4473.189
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.16 | 447 | 71.52
1007 | Helper/Khallasi | day | 0.67 | 368 | 246.56
| Total (B) |  |  |  | 541.58
| Total of (A+B) |  |  |  | 5014.769
| OVERHEADS & PROFIT @ 15 % |  |  |  | 752.22
| Total |  |  |  | 5766.989
| Rate per each |  |  |  | 5766.989
| Say |  |  |  | 5767
5767
Analysis of rate
16.11
16.11.2 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Non - Return Valve with dual plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating as specified.
16.11.2.3 | Non - Return Valve of 125mm dia |  | DSR | Rate Rs. | 4553
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3042 | 125mm dia. | Each | 1 | 3361.58 | 3361.58
| add for cartage etc. @ 1% |  |  |  | 33.6158
| Total A |  |  |  | 3395.1958
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.19 | 447 | 84.93
1007 | Helper/Khallasi | day | 0.69 | 368 | 253.92
| Total (B) |  |  |  | 562.35
| Total of (A+B) |  |  |  | 3957.5458
| OVERHEADS & PROFIT @ 15 % |  |  |  | 593.63
| Total |  |  |  | 4551.1758
| Rate per each |  |  |  | 4551.1758
| Say |  |  |  | 4551
4551
Analysis of rate
16.11
16.11.2 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Non - Return Valve with dual plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating as specified.
16.11.2.4 | Non - Return Valve of 100mm dia |  | DSR | Rate Rs. | 3327
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3043 | 100 mm dia | Each | 1 | 2294.25 | 2294.25
| add for cartage etc. @ 1% |  |  |  | 22.9425
| Total A |  |  |  | 2317.1925
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1087 | Welder | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.71 | 368 | 261.28
| Total (B) |  |  |  | 574.18
| Total of (A+B) |  |  |  | 2891.3725
| OVERHEADS & PROFIT @ 15 % |  |  |  | 433.71
| Total |  |  |  | 3325.0825
| Rate per each |  |  |  | 3325.0825
| Say |  |  |  | 3325
3325
Analysis of rate
16.11
16.11.2 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Non - Return Valve with dual plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating as specified.
16.11.2.5 | Non - Return Valve of 80mm dia |  | DSR | Rate Rs. | 2392
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3044 | 80mm dia. | Each | 1 | 1680.79 | 1680.79
| add for cartage etc. @ 1% |  |  |  | 16.8079
| Total A |  |  |  | 1697.5979
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.32 | 447 | 143.04
1087 | Welder | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.47 | 368 | 172.96
| Total (B) |  |  |  | 383.05
| Total of (A+B) |  |  |  | 2080.6479
| OVERHEADS & PROFIT @ 15 % |  |  |  | 312.1
| Total |  |  |  | 2392.7479
| Rate per each |  |  |  | 2392.7479
| Say |  |  |  | 2393
2393
Analysis of rate
16.11
16.11.2 | Supplying, fixing, testing and commissioning of following size valves, gauges and strainers for condenser water circulation as per specifications. Non - Return Valve with dual plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating as specified.
16.11.2.6 | Non - Return Valve of 65mm dia |  | DSR | Rate Rs. | 2058
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price (Valve)
3045 | 65 mm dia | Each | 1 | 1386.53 | 1386.53
| add for cartage etc. @ 1% |  |  |  | 13.8653
| Total A |  |  |  | 1400.3953
(B) LABOUR
For fixing
1004 | Fitter, Grade 1 | day | 0.32 | 447 | 143.04
1087 | Welder | day | 0.15 | 447 | 67.05
1007 | Helper/Khallasi | day | 0.48 | 368 | 176.64
| Total (B) |  |  |  | 386.73
| Total of (A+B) |  |  |  | 1787.1253
| OVERHEADS & PROFIT @ 15 % |  |  |  | 268.07
| Total |  |  |  | 2055.1953
| Rate per each |  |  |  | 2055.1953
| Say |  |  |  | 2055
2055
16.12 | DUCTING, GRILLS,DIFFUSER AND INSULATION
Analysis of rate
16.12.1 | Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
16.12.1.1 | Factory fabricated GSS sheet metal rectangular ducting as per IS 655-2006 |  | DSR | Rate Rs. | 739
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of Duct
3056 | Thickness 0.63 mm sheet | sqmtr | 10 | 430.35 | 4303.5
| add supports like MS angles, channels, rods, anchor bolts and other accessories etc. @ 15% |  |  |  | 645.525
| Total A |  |  |  | 4949.025
| B (CARTAGE) @ 1% |  |  |  | 49.4902
| Total of (A+B) |  |  |  | 4998.5152
C (LABOUR)
| For boxing of L-section. @ 5% |  |  |  | 249.9258
For fixing
1004 | Fitter, Grade 1 | day | 1.45 | 447 | 648.15
1007 | Helper/Khallasi | day | 1.45 | 368 | 533.6
| Total (C) |  |  |  | 1431.6758
| Total of (A+B+C) |  |  |  | 6430.191
| OVERHEADS & PROFIT @ 15 % |  |  |  | 964.53
| Total |  |  |  | 7394.721
| Rate per metre |  |  |  | 739.4721
| Say |  |  |  | 739
739
Analysis of rate
16.12.1 | Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
16.12.1.2 | Factory fabricated GSS sheet metal rectangular ducting as per IS 655-2006 |  | DSR | Rate Rs. | 905
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of Duct
3057 | Thickness 0.80 mm sheet | sqmtr | 10 | 548.26 | 5482.6
| add supports like MS angles, channels, rods, anchor bolts and other accessories etc. @ 15% |  |  |  | 822.39
| Total A |  |  |  | 6304.99
| B (CARTAGE) @ 1% |  |  |  | 63.0499
| Total of (A+B) |  |  |  | 6368.0399
C (LABOUR)
| For boxing of L-section. @ 5% |  |  |  | 318.402
For fixing
1004 | Fitter, Grade 1 | day | 1.45 | 447 | 648.15
1007 | Helper/Khallasi | day | 1.45 | 368 | 533.6
| Total (C) |  |  |  | 1500.152
| Total of (A+B+C) |  |  |  | 7868.1919
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1180.23
| Total |  |  |  | 9048.4219
| Rate per metre |  |  |  | 904.8422
| Say |  |  |  | 905
905
Analysis of rate
16.12.1 | Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
16.12.1.3 | Factory fabricated GSS sheet metal rectangular ducting as per IS 655-2006 |  | DSR | Rate Rs. | 1014
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of Duct
3058 | Thickness 1.00 mm sheet | sqmtr | 10 | 654.37 | 6543.7
| add supports like MS angles, channels, rods, anchor bolts and other accessories etc. @ 15% |  |  |  | 981.555
| Total A |  |  |  | 7525.255
| B (CARTAGE) @ 1% |  |  |  | 75.2525
| Total of (A+B) |  |  |  | 7600.5076
C (LABOUR)
| For boxing of L-section. @ 5% |  |  |  | 380.0254
For fixing
1004 | Fitter, Grade 1 | day | 1.03 | 447 | 460.41
1007 | Helper/Khallasi | day | 1.03 | 368 | 379.04
| Total (C) |  |  |  | 1219.4754
| Total of (A+B+C) |  |  |  | 8819.9829
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1323
| Total |  |  |  | 10142.9829
| Rate per metre |  |  |  | 1014.2983
| Say |  |  |  | 1014
1014
Analysis of rate
16.12.1 | Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
16.12.1.4 | Factory fabricated GSS sheet metal rectangular ducting as per IS 655-2006 |  | DSR | Rate Rs. | 1278
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of Duct
3059 | Thickness 1.25 mm sheet | sqmtr | 10 | 766.38 | 7663.8
| add supports like MS angles, channels, rods, anchor bolts and other accessories etc. @ 15% |  |  |  | 1149.57
| Total A |  |  |  | 8813.37
| B (CARTAGE) @ 1% |  |  |  | 88.1337
| Total of (A+B) |  |  |  | 8901.5037
C (LABOUR)
| For boxing of L-section. @ 5% |  |  |  | 445.0752
For fixing
1004 | Fitter, Grade 1 | day | 2.17 | 447 | 969.99
1007 | Helper/Khallasi | day | 2.17 | 368 | 798.56
| Total (C) |  |  |  | 2213.6252
| Total of (A+B+C) |  |  |  | 11115.1289
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1667.27
| Total |  |  |  | 12782.3989
| Rate per metre |  |  |  | 1278.2399
| Say |  |  |  | 1278
1278
Analysis of rate
16.12.2 | Supply, installation, balancing and commissioning of site fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
16.12.2.1 | Factory fabricated GSS sheet metal rectangular ducting as per IS 655-2006 for 0.63 mm thick |  | DSR | Rate Rs. | 630
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of sheet
3060 | Thickness 0.63 mm sheet | sqmtr | 10 | 310.86 | 3108.6
| add wastage @ 10% |  |  |  | 310.86
| Total A |  |  |  | 3419.46
| B (CARTAGE) @ 1% |  |  |  | 34.1946
| Total of (A+B) |  |  |  | 3453.6546
C (LABOUR)
For fabrication
1004 | Fitter, Grade 1 | day | 1.48 | 447 | 661.56
1007 | Helper/Khallasi | day | 1.48 | 368 | 544.64
For fixing
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total (C) |  |  |  | 2021.2
| Total of (A+B+C) |  |  |  | 5474.8546
| OVERHEADS & PROFIT @ 15 % |  |  |  | 821.23
| Total |  |  |  | 6296.0846
| Rate per metre |  |  |  | 629.6085
| Say |  |  |  | 630
630
Analysis of rate
16.12.2 | Supply, installation, balancing and commissioning of site fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
16.12.2.2 | Factory fabricated GSS sheet metal rectangular ducting as per IS 655-2006 for 0.8 mm thick |  | DSR | Rate Rs. | 752
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of sheet
3061 | Thickness 0.80 mm sheet | sqmtr | 10 | 414.48 | 4144.8
| add wastage @ 10% |  |  |  | 414.48
| Total A |  |  |  | 4559.28
| B (CARTAGE) @ 1% |  |  |  | 45.5928
| Total of (A+B) |  |  |  | 4604.8728
C (LABOUR)
For fabrication
1004 | Fitter, Grade 1 | day | 1.48 | 447 | 661.56
1007 | Helper/Khallasi | day | 1.48 | 368 | 544.64
For fixing
1004 | Fitter, Grade 1 | day | 0.89 | 447 | 397.83
1007 | Helper/Khallasi | day | 0.89 | 368 | 327.52
| Total (C) |  |  |  | 1931.55
| Total of (A+B+C) |  |  |  | 6536.4228
| OVERHEADS & PROFIT @ 15 % |  |  |  | 980.46
| Total |  |  |  | 7516.8828
| Rate per metre |  |  |  | 751.6883
| Say |  |  |  | 752
752
Analysis of rate
16.12.2 | Supply, installation, balancing and commissioning of site fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
16.12.2.3 | Factory fabricated GSS sheet metal rectangular ducting as per IS 655-2006 for 1.00 mm thick |  | DSR | Rate Rs. | 983
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of sheet
3062 | Thickness 1.00 mm sheet | sqmtr | 10 | 518.1 | 5181
| add wastage @ 10% |  |  |  | 518.1
| Total A |  |  |  | 5699.1
| B (CARTAGE) @ 1% |  |  |  | 56.991
| Total of (A+B) |  |  |  | 5756.091
C (LABOUR)
For fabrication
1004 | Fitter, Grade 1 | day | 2 | 447 | 894
1007 | Helper/Khallasi | day | 2 | 368 | 736
For fixing
1004 | Fitter, Grade 1 | day | 1.43 | 447 | 639.21
1007 | Helper/Khallasi | day | 1.43 | 368 | 526.24
| Total (C) |  |  |  | 2795.45
| Total of (A+B+C) |  |  |  | 8551.541
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1282.73
| Total |  |  |  | 9834.271
| Rate per metre |  |  |  | 983.4271
| Say |  |  |  | 983
983
Analysis of rate
16.12.2 | Supply, installation, balancing and commissioning of site fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
16.12.2.4 | Factory fabricated GSS sheet metal rectangular ducting as per IS 655-2006 for 1.00 mm thick |  | DSR | Rate Rs. | 1104
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of sheet
3063 | Thickness 1.25 mm sheet | sqmtr | 10 | 627 | 6270
| add wastage @ 10% |  |  |  | 627
| Total A |  |  |  | 6897
| B (CARTAGE) @ 1% |  |  |  | 68.97
| Total of (A+B) |  |  |  | 6965.97
C (LABOUR)
For fabrication
1004 | Fitter, Grade 1 | day | 1.8 | 447 | 804.6
1007 | Helper/Khallasi | day | 1.8 | 368 | 662.4
For fixing
1004 | Fitter, Grade 1 | day | 1.43 | 447 | 639.21
1007 | Helper/Khallasi | day | 1.43 | 368 | 526.24
| Total (C) |  |  |  | 2632.45
| Total of (A+B+C) |  |  |  | 9598.42
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1439.76
| Total |  |  |  | 11038.18
| Rate per metre |  |  |  | 1103.818
| Say |  |  |  | 1104
1104
Analysis of rate
16.13 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications.
| GI volume control duct damper |  | DSR | Rate Rs. | 5463
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
3064 | GI volume control duct damper | sqmtr | 1 | 4300 | 4300
| add cartage @ 1% |  |  |  | 43
| Total A |  |  |  | 4343
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total (C) |  |  |  | 407.5
| Total of (A+B) |  |  |  | 4750.5
| OVERHEADS & PROFIT @ 15 % |  |  |  | 712.58
| Total |  |  |  | 5463.08
| Rate per each |  |  |  | 5463.08
| Say |  |  |  | 5463
5463
Analysis of rate
16.14 | Supply, installation, testing and commissioning of Motorized (ON-OFF Type) duct mounted GI volume control damper with enthalpy sensor and necessary control wire (minimum 1.5 sqmm) for integration within AHU room.
16.14.1 | Motorized (ON-OFF Type) duct mounted GI volume control damper |  | DSR | Rate Rs. | 6308
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
3064 | GI volume control duct damper | sqmtr | 1 | 4300 | 4300
| add cartage @ 1% |  |  |  | 43
| Total A |  |  |  | 4343
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1001 | Wireman | day | 0.9 | 447 | 402.3
1007 | Helper/Khallasi | day | 1.4 | 368 | 515.2
| Total (C) |  |  |  | 1141
| Total of (A+B) |  |  |  | 5484
| OVERHEADS & PROFIT @ 15 % |  |  |  | 822.6
| Total |  |  |  | 6306.6
| Rate per each |  |  |  | 6306.6
| Say |  |  |  | 6307
6307
Analysis of rate
16.14 | Supply, installation, testing and commissioning of Motorized (ON-OFF Type) duct mounted GI volume control damper with enthalpy sensor and necessary control wire (minimum 1.5 sqmm) for integration within AHU room.
16.14.2 | Motorized (ON-OFF Type) duct mounted GI volume control actuator |  | DSR | Rate Rs. | 5483
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
3065 | Actuator | sqmtr | 1 | 3589 | 3589
| add cartage @ 1% |  |  |  | 35.89
| Total A |  |  |  | 3624.89
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1001 | Wireman | day | 0.9 | 447 | 402.3
1007 | Helper/Khallasi | day | 1.4 | 368 | 515.2
| Total (C) |  |  |  | 1141
| Total of (A+B) |  |  |  | 4765.89
| OVERHEADS & PROFIT @ 15 % |  |  |  | 714.88
| Total |  |  |  | 5480.77
| Rate per each |  |  |  | 5480.77
| Say |  |  |  | 5481
5481
Analysis of rate
16.15 | Supplying & fixing of powder coated extruded aluminium Supply Air Grills with aluminium volume control dampers as per specifications.
|  |  | DSR | Rate Rs. | 7132
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
3066 | powder coated extruded aluminium Supply Air Grills with aluminium volume control dampers | sqmtr | 10 | 5912.68 | 59126.8
| add for cartage etc. @ 1% |  |  |  | 591.268
| add for screws etc. | LS |  |  | 260
| Total A |  |  |  | 59978.068
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1007 | Helper/Khallasi | day | 2.5 | 368 | 920
| Total (C) |  |  |  | 2037.5
| Total of (A+B) |  |  |  | 62015.568
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9302.34
| Total |  |  |  | 71317.908
| Rate per metre |  |  |  | 7131.7908
| Say |  |  |  | 7132
7132
Analysis of rate
16.16 | Supplying & fixing of powder coated extruded aluminium Return Air Grills with louvers but without volume control dampers complete as required.
|  |  | DSR | Rate Rs. | 4065
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
3067 | powder coated extruded aluminium Return Air Grills with louvers but without volume control dampers | sqmtr | 10 | 3272.43 | 32724.3
| add for cartage etc. @ 1% |  |  |  | 327.243
| add for screws etc. | LS |  |  | 260
| Total A |  |  |  | 33311.543
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1007 | Helper/Khallasi | day | 2.5 | 368 | 920
| Total (C) |  |  |  | 2037.5
| Total of (A+B) |  |  |  | 35349.043
| OVERHEADS & PROFIT @ 15 % |  |  |  | 5302.36
| Total |  |  |  | 40651.403
| Rate per metre |  |  |  | 4065.1403
| Say |  |  |  | 4065
4065
Analysis of rate
16.17 | Supplying, fixing testing commissioning of supply air diffusers of powder coated aluminium with aluminium volume control dampers with anti smudge ring & removable core.
|  |  | DSR | Rate Rs. | 8686
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
3068 | supply air diffusers of powder coated aluminium with aluminium volume control dampers with anti smudge ring & removable core. | sqmtr | 10 | 7251.4 | 72514
| add for cartage etc. @ 1% |  |  |  | 725.14
| add for screws etc. | LS |  |  | 250
| Total A |  |  |  | 73489.14
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1007 | Helper/Khallasi | day | 2.5 | 368 | 920
| Total (C) |  |  |  | 2037.5
| Total of (A+B) |  |  |  | 75526.64
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11329
| Total |  |  |  | 86855.64
| Rate per metre |  |  |  | 8685.564
| Say |  |  |  | 8686
8686
Analysis of rate
16.18 | Supplying, fixing testing commissioning of Return air diffusers of powder coated aluminium without volume control dampers with anti smudge ring & removable core.
|  |  | DSR | Rate Rs. | 5619
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
3069 | Return air diffusers of powder coated aluminium without volume control dampers with anti smudge ring & removable core. | sqmtr | 10 | 4611.15 | 46111.5
| add for cartage etc. @ 1% |  |  |  | 461.115
| add for screws etc. | LS |  |  | 250
| Total A |  |  |  | 46822.615
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 2.5 | 447 | 1117.5
1007 | Helper/Khallasi | day | 2.5 | 368 | 920
| Total (C) |  |  |  | 2037.5
| Total of (A+B) |  |  |  | 48860.115
| OVERHEADS & PROFIT @ 15 % |  |  |  | 7329.02
| Total |  |  |  | 56189.135
| Rate per metre |  |  |  | 5618.9135
| Say |  |  |  | 5619
5619
Analysis of rate
16.19 | Supply, installation, testing & commissioning of thermal insulated flexible duct of following sizes duly supported at regular interval as per site requirement etc. complete as required as per specifications.
16.19.1 | Thermal insulated flexible duct (200mm dia) |  | DSR | Rate Rs. | 381
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
3070 | Thermal insulated flexible duct- 200 mm dia | sqmtr | 10 | 274 | 2740
| add for support etc. @ 5% |  |  |  | 137
| Total |  |  |  | 2877
| add for cartage etc. @ 1% |  |  |  | 28.77
| Total A |  |  |  | 2905.77
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total (C) |  |  |  | 407.5
| Total of (A+B) |  |  |  | 3313.27
| OVERHEADS & PROFIT @ 15 % |  |  |  | 496.99
| Total |  |  |  | 3810.26
| Rate per metre |  |  |  | 381.026
| Say |  |  |  | 381
381
Analysis of rate
16.20 | Supplying, Fixing, testing and commissioning of fire dampers in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring, the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications.
16.20.1 | Fire damper |  | DSR | Rate Rs. | 7103
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
3071 | Fire damper | sqmtr | 1 | 5711.87 | 5711.87
| add for cartage etc. @ 1% |  |  |  | 57.1187
| Total A |  |  |  | 5768.9887
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total (C) |  |  |  | 407.5
| Total of (A+B) |  |  |  | 6176.4887
| OVERHEADS & PROFIT @ 15 % |  |  |  | 926.47
| Total |  |  |  | 7102.9587
| Rate per metre |  |  |  | 7102.9587
| Say |  |  |  | 7103
7103
Analysis of rate
16.20 | Supplying, Fixing, testing and commissioning of fire dampers in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring, the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications.
16.20.2 | Actuator |  | DSR | Rate Rs. | 6604
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
3072 | Actuator | sqmtr | 1 | 5255.72 | 5255.72
| add for cartage etc. @ 1% |  |  |  | 52.5572
| Total A |  |  |  | 5308.2772
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1001 | Wireman | day | 0.04 | 447 | 17.88
1007 | Helper/Khallasi | day | 0.53 | 368 | 195.04
| Total (C) |  |  |  | 436.42
| Total of (A+B) |  |  |  | 5744.6972
| OVERHEADS & PROFIT @ 15 % |  |  |  | 861.7
| Total |  |  |  | 6606.3972
| Rate per metre |  |  |  | 6606.3972
| Say |  |  |  | 6606
6606
Analysis of rate
16.21 | Supplying, Fixing, testing and commissioning of fire dampers in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring, the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications.
| Acoustic lining of supply air duct with 25mm thick resin bonded glass wool having density of 32kg/m3 |  | DSR | Rate Rs. | 551
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
4069 | Acoustic lining of supply air duct with 25mm thick resin bonded glass wool having density of 32kg/m3 | Sqmtr | 10 | 152 | 1520
| add wastage @ 15% |  |  |  | 228
| Total |  |  |  | 1748
| add for framework of aluminium channel etc. @ 25% |  |  |  | 380
| Total |  |  |  | 2128
4070 | Reinforced fiber glass tissue and 0 08mm perforated aluminium sheet | Sqmtr | 10 | 260 | 2600
| Total |  |  |  | 4728
| add for cartage etc. @ 1% |  |  |  | 47.28
| Total of A |  |  |  | 4775.28
B (LABOUR)
For lining works
1004 | Fitter, Grade 1 | day | 0.6 | 447 | 268.2
1007 | Helper/Khallasi | day | 0.6 | 368 | 220.8
| Total of B(1) |  |  |  | 489
For insulation work
1004 | Fitter, Grade 1 | day | 0.3 | 447 | 134.1
1007 | Helper/Khallasi | day | 0.3 | 368 | 110.4
| Total of B() |  |  |  | 244.5
| Total |  |  |  | 733.5
| Total of (A+B) |  |  |  | 5508.78
| OVERHEADS & PROFIT @ 0 % |  |  |  | 0
| Total |  |  |  | 5508.78
| Rate per metre |  |  |  | 550.878
| Say |  |  |  | 551
551
Analysis of rate
16.22 | Supplying, fixing acoustic lining on wall and ceiling of AHU rooms with 50mm thick, density 32 kg/cu.m resin bonded glass fiber insulation friction fixed in 610mm x 610 mm frame work made of 25X50X50X50X25 mm made out of 0.6mm thick GI sheet U shaped channel and covered with reinforced fiber glass tissue and finished with 0.80 mm perforated aluminium sheet etc. complete as required and as per specifications.
| 50 mm thick resin bonded glass wool having denary of 32kg/m3 |  | DSR | Rate Rs. | 870
Details of cost for 10 Metres
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of
4071 | 50 mm thick resin bonded glass wool having denary of 32kg/m3 | Sqmtr | 10 | 196.02 | 1960.2
| add wastage @ 10% |  |  |  | 196.02
| Total |  |  |  | 2156.22
| add for adhesive compound and tape etc. @ 05% |  |  |  | 107.811
| Total |  |  |  | 2264.031
| add for framework of aluminium channel etc. @ 25% |  |  |  | 566.0078
| Total |  |  |  | 2830.0388
4070 | Reinforced fiber glass tissue and 0 08mm perforated aluminium sheet | Sqmtr | 10 | 260 | 2600
| Total |  |  |  | 5430.0388
| add for cartage etc. @ 1% |  |  |  | 54.3004
| Total of A |  |  |  | 5484.3391
B (LABOUR)
For lining works
1004 | Fitter, Grade 1 | day | 0.4 | 447 | 178.8
1007 | Helper/Khallasi | day | 0.4 | 368 | 147.2
| Total of B(1) |  |  |  | 326
For insulation work
1004 | Fitter, Grade 1 | day | 0.2 | 447 | 89.4
1007 | Helper/Khallasi | day | 0.2 | 368 | 73.6
| Total of B() |  |  |  | 163
| Total |  |  |  | 489
| Total of (A+B) |  |  |  | 5973.3391
| OVERHEADS & PROFIT @ 0 % |  |  |  | 0
| Total |  |  |  | 5973.3391
| Rate per metre |  |  |  | 597.3339
| Say |  |  |  | 597
597
Analysis of rate
16.23 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber (class “O”) insulation on existing duct after applying two coats of cold setting adhesive (CPRX compound). The joints shall sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
16.23.1 | Nitrile rubber insulation - 19 mm |  | DSR | Rate Rs. | 821
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of Nitrile rubber insulation
3076 | 19mmthickness | sqmtr | 10 | 605.55 | 6055.5
| add wastage @ 05% |  |  |  | 302.775
| Total |  |  |  | 6358.275
| add for adhesive compound and tape etc. @ 05% |  |  |  | 302.775
| Total A |  |  |  | 6661.05
| add for cartage etc. @ 1% |  |  |  | 66.6105
| Total A |  |  |  | 6727.6605
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total (C) |  |  |  | 407.5
| Total of (A+B) |  |  |  | 7135.1605
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1070.27
| Total |  |  |  | 8205.4305
| Rate per metre |  |  |  | 820.543
| Say |  |  |  | 821
821
Analysis of rate
16.23 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber (class “O”) insulation on existing duct after applying two coats of cold setting adhesive (CPRX compound). The joints shall sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
16.23.2 | Nitrile rubber insulation - 25 mm |  | DSR | Rate Rs. | 1034
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price of Nitrile rubber insulation
3077 | 25mmthickness | sqmtr | 10 | 772.75 | 7727.5
| add wastage @ 05% |  |  |  | 386.375
| Total |  |  |  | 8113.875
| add for adhesive compound and tape etc. @ 05% |  |  |  | 386.375
| Total A |  |  |  | 8500.25
| add for cartage etc. @ 1% |  |  |  | 85.0025
| Total A |  |  |  | 8585.2525
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 0.5 | 447 | 223.5
1007 | Helper/Khallasi | day | 0.5 | 368 | 184
| Total (C) |  |  |  | 407.5
| Total of (A+B) |  |  |  | 8992.7525
| OVERHEADS & PROFIT @ 15 % |  |  |  | 1348.91
| Total |  |  |  | 10341.6625
| Rate per metre |  |  |  | 1034.1662
| Say |  |  |  | 1034
1034
Analysis of rate
16.24 | Supplying and fixing 50 mm thick aluminium foil faced resin bonded fibre glass insulation (on duct ) of density 24 kg/ cu.m after applying two coats of cold setting adhesive (CPRX compound) sealing all joints with self adhesive aluminium tape & covering with 0.63mmx19mm GI wire mesh netting butting all joints and laced with GI wire complete as per specifications and as required. (for indoor applications).
| 50 mm thick resin bonded glass wool having density of 24 kg/m3 |  | DSR | Rate Rs. | 378
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price
4072 | 50 mm thick resin bonded glass wool having density of 24 kg/m3 | Sqmtr | 10 | 193.45 | 1934.5
| add wastage @ 10% |  |  |  | 193.45
| Total |  |  |  | 2127.95
| add for adhesive compound and tape and wire mesh etc. @ 15% |  |  |  | 319.1925
| Total A |  |  |  | 2447.1425
| add for cartage etc. @ 1% |  |  |  | 24.4714
| Total A |  |  |  | 2471.6139
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total (C) |  |  |  | 815
| Total of (A+B) |  |  |  | 3286.6139
| OVERHEADS & PROFIT @ 15 % |  |  |  | 492.99
| Total |  |  |  | 3779.6039
| Rate per metre |  |  |  | 377.9604
| Say |  |  |  | 378
378
Analysis of rate
16.25 | Supplying and fixing 50mm thick aluminium foil faced resin bonded fibre glass insulation (on duct) of density 24 kg/ cu.m after applying two coats of cold setting adhesive (CPRX compound) sealing all joints with self adhesive aluminium tape & covering with 0.63mmx19mm GI wire mesh netting & butting all joints and laced with GI wire complete and finally covered with one layer of tar felt stuck with hot bitumen as per specifications and as required. (for outdoor applications)
| 50 mm thick resin bonded glass wool having density of 24 kg/m3 |  | DSR | Rate Rs. | 437
Details of cost for 10 Metres Duct
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price
4072 | 50 mm thick resin bonded glass wool having density of 24 kg/m3 | Sqmtr | 10 | 193.45 | 1934.5
| add wastage @ 10% |  |  |  | 193.45
| Total |  |  |  | 2127.95
| add for adhesive compound and tape and wire mesh etc. @ 15% |  |  |  | 319.1925
| Total A |  |  |  | 2447.1425
| add for cartage etc. @ 1% |  |  |  | 24.4714
| Total A |  |  |  | 2471.6139
B (LABOUR)
For fixing
1004 | Fitter, Grade 1 | day | 1 | 447 | 447
1007 | Helper/Khallasi | day | 1 | 368 | 368
| Total (C) |  |  |  | 815
| Total of (A+B) |  |  |  | 3286.6139
| LS for bitumin and Tar felt |  |  |  | 590
| Total |  |  |  | 3876.6139
| OVERHEADS & PROFIT @ 15 % |  |  |  | 492.99
| Total |  |  |  | 4369.6039
| Rate per metre |  |  |  | 436.9604
| Say |  |  |  | 437
437
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.1 | Basic Price Double skin AHU Units of 6 row cooling coil of 2500CFM |  | DSR | Rate Rs. | 75410
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3078 | 2500CFM | Each | 1 | 61249.85 | 61249.85
| add for cartage etc. @ 1% |  |  |  | 612.4985
| Total |  |  |  | 61862.3485
| ITC @ 6% of A |  |  |  | 3711.7409
| Total A |  |  |  | 65574.0894
| OVERHEADS & PROFIT @ 15 % |  |  |  | 9836.11
| Total |  |  |  | 75410.1994
| Rate for each |  |  |  | 75410.1994
| Say |  |  |  | 75410
75410
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.2 | Basic Price Double skin AHU Units of 6 row cooling coil of 3000CFM |  | DSR | Rate Rs. | 88718
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3079 | 3000CFM | Each | 1 | 72058.65 | 72058.65
| add for cartage etc. @ 1% |  |  |  | 720.5865
| Total |  |  |  | 72779.2365
| ITC @ 6% of A |  |  |  | 4366.7542
| Total A |  |  |  | 77145.9907
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11571.9
| Total |  |  |  | 88717.8907
| Rate for each |  |  |  | 88717.8907
| Say |  |  |  | 88718
88718
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.3 | Basic Price Double skin AHU Units of 6 row cooling coil of 4000CFM |  | DSR | Rate Rs. | 100009
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3080 | 4000CFM | Each | 1 | 81229.75 | 81229.75
| add for cartage etc. @ 1% |  |  |  | 812.2975
| Total |  |  |  | 82042.0475
| ITC @ 6% of A |  |  |  | 4922.5229
| Total A |  |  |  | 86964.5703
| OVERHEADS & PROFIT @ 15 % |  |  |  | 13044.69
| Total |  |  |  | 100009.2603
| Rate for each |  |  |  | 100009.2603
| Say |  |  |  | 100009
100009
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.4 | Basic Price Double skin AHU Units of 6 row cooling coil of 5000CFM |  | DSR | Rate Rs. | 124770
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3081 | 5000CFM | Each | 1 | 101340.66 | 101340.66
| add for cartage etc. @ 1% |  |  |  | 1013.4066
| Total |  |  |  | 102354.0666
| ITC @ 6% of A |  |  |  | 6141.244
| Total A |  |  |  | 108495.3106
| OVERHEADS & PROFIT @ 15 % |  |  |  | 16274.3
| Total |  |  |  | 124769.6106
| Rate for each |  |  |  | 124769.6106
| Say |  |  |  | 124770
124770
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.5 | Basic Price Double skin AHU Units of 6 row cooling coil of 6000CFM |  | DSR | Rate Rs. | 145901
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3082 | 6000CFM | Each | 1 | 118503.72 | 118503.72
| add for cartage etc. @ 1% |  |  |  | 1185.0372
| Total |  |  |  | 119688.7572
| ITC @ 6% of A |  |  |  | 7181.3254
| Total A |  |  |  | 126870.0826
| OVERHEADS & PROFIT @ 15 % |  |  |  | 19030.51
| Total |  |  |  | 145900.5926
| Rate for each |  |  |  | 145900.5926
| Say |  |  |  | 145901
145901
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.6 | Basic Price Double skin AHU Units of 6 row cooling coil of 7000CFM |  | DSR | Rate Rs. | 163967
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3083 | 7000CFM | Each | 1 | 133177.48 | 133177.48
| add for cartage etc. @ 1% |  |  |  | 1331.7748
| Total |  |  |  | 134509.2548
| ITC @ 6% of A |  |  |  | 8070.5553
| Total A |  |  |  | 142579.8101
| OVERHEADS & PROFIT @ 15 % |  |  |  | 21386.97
| Total |  |  |  | 163966.7801
| Rate for each |  |  |  | 163966.7801
| Say |  |  |  | 163967
163967
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.7 | Basic Price Double skin AHU Units of 6 row cooling coil of 8000CFM |  | DSR | Rate Rs. | 182033
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3084 | 8000CFM | Each | 1 | 147851.24 | 147851.24
| add for cartage etc. @ 1% |  |  |  | 1478.5124
| Total |  |  |  | 149329.7524
| ITC @ 6% of A |  |  |  | 8959.7851
| Total A |  |  |  | 158289.5375
| OVERHEADS & PROFIT @ 15 % |  |  |  | 23743.43
| Total |  |  |  | 182032.9675
| Rate for each |  |  |  | 182032.9675
| Say |  |  |  | 182033
182033
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.8 | Basic Price Double skin AHU Units of 6 row cooling coil of 9000CFM |  | DSR | Rate Rs. | 199212
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3085 | 9000CFM | Each | 1 | 161804.41 | 161804.41
| add for cartage etc. @ 1% |  |  |  | 1618.0441
| Total |  |  |  | 163422.4541
| ITC @ 6% of A |  |  |  | 9805.3472
| Total A |  |  |  | 173227.8013
| OVERHEADS & PROFIT @ 15 % |  |  |  | 25984.17
| Total |  |  |  | 199211.9713
| Rate for each |  |  |  | 199211.9713
| Say |  |  |  | 199212
199212
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.9 | Basic Price Double skin AHU Units of 6 row cooling coil of 10000CFM |  | DSR | Rate Rs. | 216391
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3086 | 10000CFM | Each | 1 | 175757.59 | 175757.59
| add for cartage etc. @ 1% |  |  |  | 1757.5759
| Total |  |  |  | 177515.1659
| ITC @ 6% of A |  |  |  | 10650.91
| Total A |  |  |  | 188166.0759
| OVERHEADS & PROFIT @ 15 % |  |  |  | 28224.91
| Total |  |  |  | 216390.9859
| Rate for each |  |  |  | 216390.9859
| Say |  |  |  | 216391
216391
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.10 | Basic Price Double skin AHU Units of 6 row cooling coil of 11000CFM |  | DSR | Rate Rs. | 237683
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3087 | 11000CFM | Each | 1 | 193051.66 | 193051.66
| add for cartage etc. @ 1% |  |  |  | 1930.5166
| Total |  |  |  | 194982.1766
| ITC @ 6% of A |  |  |  | 11698.9306
| Total A |  |  |  | 206681.1072
| OVERHEADS & PROFIT @ 15 % |  |  |  | 31002.17
| Total |  |  |  | 237683.2772
| Rate for each |  |  |  | 237683.2772
| Say |  |  |  | 237683
237683
Analysis of rate
16.26 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 6 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.26.11 | Basic Price Double skin AHU Units of 6 row cooling coil of 12000CFM |  | DSR | Rate Rs. | 258976
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 6 row cooling coil of
3088 | 12000CFM | Each | 1 | 210345.74 | 210345.74
| add for cartage etc. @ 1% |  |  |  | 2103.4574
| Total |  |  |  | 212449.1974
| ITC @ 6% of A |  |  |  | 12746.9518
| Total A |  |  |  | 225196.1492
| OVERHEADS & PROFIT @ 15 % |  |  |  | 33779.42
| Total |  |  |  | 258975.5692
| Rate for each |  |  |  | 258975.5692
| Say |  |  |  | 258976
258976
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.1 | Basic Price Double skin AHU Units of 4 row cooling coil of 2500CFM |  | DSR | Rate Rs. | 68232
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3089 | 2500CFM | Each | 1 | 55419.65 | 55419.65
| add for cartage etc. @ 1% |  |  |  | 554.1965
| Total |  |  |  | 55973.8465
| ITC @ 6% of A |  |  |  | 3358.4308
| Total A |  |  |  | 59332.2773
| OVERHEADS & PROFIT @ 15 % |  |  |  | 8899.84
| Total |  |  |  | 68232.1173
| Rate for each |  |  |  | 68232.1173
| Say |  |  |  | 68232
68232
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.2 | Basic Price Double skin AHU Units of 4 row cooling coil of 3000CFM |  | DSR | Rate Rs. | 80088
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3090 | 3000CFM | Each | 1 | 65049.3 | 65049.3
| add for cartage etc. @ 1% |  |  |  | 650.493
| Total |  |  |  | 65699.793
| ITC @ 6% of A |  |  |  | 3941.9876
| Total A |  |  |  | 69641.7806
| OVERHEADS & PROFIT @ 15 % |  |  |  | 10446.27
| Total |  |  |  | 80088.0506
| Rate for each |  |  |  | 80088.0506
| Say |  |  |  | 80088
80088
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.3 | Basic Price Double skin AHU Units of 4 row cooling coil of 4000CFM |  | DSR | Rate Rs. | 89363
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3091 | 4000CFM | Each | 1 | 72582.71 | 72582.71
| add for cartage etc. @ 1% |  |  |  | 725.8271
| Total |  |  |  | 73308.5371
| ITC @ 6% of A |  |  |  | 4398.5122
| Total A |  |  |  | 77707.0493
| OVERHEADS & PROFIT @ 15 % |  |  |  | 11656.06
| Total |  |  |  | 89363.1093
| Rate for each |  |  |  | 89363.1093
| Say |  |  |  | 89363
89363
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.4 | Basic Price Double skin AHU Units of 4 row cooling coil of 5000CFM |  | DSR | Rate Rs. | 110575
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3092 | 5000CFM | Each | 1 | 89811.28 | 89811.28
| add for cartage etc. @ 1% |  |  |  | 898.1128
| Total |  |  |  | 90709.3928
| ITC @ 6% of A |  |  |  | 5442.5636
| Total A |  |  |  | 96151.9564
| OVERHEADS & PROFIT @ 15 % |  |  |  | 14422.79
| Total |  |  |  | 110574.7464
| Rate for each |  |  |  | 110574.7464
| Say |  |  |  | 110575
110575
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.5 | Basic Price Double skin AHU Units of 4 row cooling coil of 6000CFM |  | DSR | Rate Rs. | 129447
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3093 | 6000CFM | Each | 1 | 105140.11 | 105140.11
| add for cartage etc. @ 1% |  |  |  | 1051.4011
| Total |  |  |  | 106191.5111
| ITC @ 6% of A |  |  |  | 6371.4907
| Total A |  |  |  | 112563.0018
| OVERHEADS & PROFIT @ 15 % |  |  |  | 16884.45
| Total |  |  |  | 129447.4518
| Rate for each |  |  |  | 129447.4518
| Say |  |  |  | 129447
129447
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.6 | Basic Price Double skin AHU Units of 4 row cooling coil of 7000CFM |  | DSR | Rate Rs. | 144812
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3094 | 7000CFM | Each | 1 | 117619.36 | 117619.36
| add for cartage etc. @ 1% |  |  |  | 1176.1936
| Total |  |  |  | 118795.5536
| ITC @ 6% of A |  |  |  | 7127.7332
| Total A |  |  |  | 125923.2868
| OVERHEADS & PROFIT @ 15 % |  |  |  | 18888.49
| Total |  |  |  | 144811.7768
| Rate for each |  |  |  | 144811.7768
| Say |  |  |  | 144812
144812
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.7 | Basic Price Double skin AHU Units of 4 row cooling coil of 8000CFM |  | DSR | Rate Rs. | 160176
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3095 | 8000CFM | Each | 1 | 130098.61 | 130098.61
| add for cartage etc. @ 1% |  |  |  | 1300.9861
| Total |  |  |  | 131399.5961
| ITC @ 6% of A |  |  |  | 7883.9758
| Total A |  |  |  | 139283.5719
| OVERHEADS & PROFIT @ 15 % |  |  |  | 20892.54
| Total |  |  |  | 160176.1119
| Rate for each |  |  |  | 160176.1119
| Say |  |  |  | 160176
160176
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.8 | Basic Price Double skin AHU Units of 4 row cooling coil of 9000CFM |  | DSR | Rate Rs. | 174573
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3096 | 9000CFM | Each | 1 | 141791.76 | 141791.76
| add for cartage etc. @ 1% |  |  |  | 1417.9176
| Total |  |  |  | 143209.6776
| ITC @ 6% of A |  |  |  | 8592.5807
| Total A |  |  |  | 151802.2583
| OVERHEADS & PROFIT @ 15 % |  |  |  | 22770.34
| Total |  |  |  | 174572.5983
| Rate for each |  |  |  | 174572.5983
| Say |  |  |  | 174573
174573
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.9 | Basic Price Double skin AHU Units of 4 row cooling coil of 10000CFM |  | DSR | Rate Rs. | 188969
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3097 | 10000CFM | Each | 1 | 153484.91 | 153484.91
| add for cartage etc. @ 1% |  |  |  | 1534.8491
| Total |  |  |  | 155019.7591
| ITC @ 6% of A |  |  |  | 9301.1855
| Total A |  |  |  | 164320.9446
| OVERHEADS & PROFIT @ 15 % |  |  |  | 24648.14
| Total |  |  |  | 188969.0846
| Rate for each |  |  |  | 188969.0846
| Say |  |  |  | 188969
188969
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.10 | Basic Price Double skin AHU Units of 4 row cooling coil of 11000CFM |  | DSR | Rate Rs. | 204858
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3098 | 11000CFM | Each | 1 | 166389.96 | 166389.96
| add for cartage etc. @ 1% |  |  |  | 1663.8996
| Total |  |  |  | 168053.8596
| ITC @ 6% of A |  |  |  | 10083.2316
| Total A |  |  |  | 178137.0912
| OVERHEADS & PROFIT @ 15 % |  |  |  | 26720.56
| Total |  |  |  | 204857.6512
| Rate for each |  |  |  | 204857.6512
| Say |  |  |  | 204858
204858
Analysis of rate
16.27 | Supply, Installation, Testing and commissioning of factory built floor mounted chilled water double skin type horizontal/ vertical air handling units made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend GSS/PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with TEFC drive motor suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.) and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration isolation arrangement etc. complete as per specification and of following capacities.
16.27.11 | Basic Price Double skin AHU Units of 4 row cooling coil of 12000CFM |  | DSR | Rate Rs. | 226150
Details of cost for Each
ICD No | Description | Unit | Qty | Rate | Amount (Rs.)
A (MATERIALS)
Basic Price Double skin AHU Units of 4 row cooling coil of
3099 | 12000CFM | Each | 1 | 183684.04 | 183684.04
| add for cartage etc. @ 1% |  |  |  | 1836.8404
| Total |  |  |  | 185520.8804
| ITC @ 6% of A |  |  |  | 11131.2528
| Total A |  |  |  | 196652.1332
| OVERHEADS & PROFIT @ 15 % |  |  |  | 29497.82
| Total |  |  |  | 226149.9532
| Rate for each |  |  |  | 226149.9532
| Say |  |  |  | 226150
226150